## Version
DOCUMENT CONTROL
Hardcoded. These values identify which generation of the template a returned file came from — never make them formulas.
Template version | 3.1.0
Released | 2026-09-03
Template name | EVSE Project Intake
Issued by | Zero Impact Energy
Template content hash | 4aecae7d4b5f25a9 | The hash of the BLANK template this file was built from, frozen at its release. It does not change when you fill the sheet in.
Completed by — fill these in
This file version | Rev A | e.g. Rev A, Rev B — increment each time you send it back
Date completed | 2026-09-02
Completed by | Test CPM
Project reference | BW-TEST-001
Notes on this revision | Fixture for the importer test | What changed since the last version you sent
File content hash | 4aecae7d4b5f25a9 | A hash of THIS workbook. It changes every time someone edits it, and it is what a model records so you can tell whether the model was built from the file in front of you.
Changelog
Version | Released | What changed
1.0.0 | 2026-08-26 | Initial release — project, equipment, electrical, construction, commercial, revenue and carbon intake with live consistency checks.
1.1.0 | 2026-08-26 | Deal structure knobs and the override register. Base case unchanged at zero.
1.2.0 | 2026-08-26 | PG&E Rule 29 interconnection capture. Electrical materials costed independently of the EVSE price book.
1.3.0 | 2026-08-26 | Utility rate engine across PG&E, SCE and SDG&E. Market benchmarks. Demand subscription ramps with concurrency.
1.4.0 | 2026-08-26 | Scope of supply controls — each service line can be provided by us, by others, or not required. Document control added.
1.5.0 | 2026-08-26 | Mixed-fleet fix — accessories no longer counted as charging units, and the placement check compares against DC cabinets only.
1.6.0 | 2026-08-26 | Description was not recorded at the time. The change sits between the mixed-fleet fix (1.5.0) and the rip-and-replace capability (1.7.0).
1.7.0 | 2026-08-26 | Rip-and-replace project type. A new Existing tab captures the existing installation, the retained-versus-replaced register, thirty-six months of usage and billing history, port and connector expansion, and the removal scope. Tabs 3, 4 and 6 respond to what is retained and can now be driven from historical actuals.
1.8.0 | 2026-08-26 | Utility selection became a dropdown of every California delivery utility — 56 investor-owned, publicly owned, tribal and cooperative entities that set their own retail tariff. New Utilities tab carries the roster and the community choice aggregators separately, because a CCA sets generation only and cannot set an EV tariff. New RateLibrary tab carries 32 researched commercial EV and fallback rates with a STATUS column, plus the utility rebate programmes and their open/closed state.
1.9.0 | 2026-08-27 | Price book states the included manufacturer warranty per charger class — two years on DC fast charging, one year on Level 2, parts only — and the out-of-warranty service column now reads NOT OFFERED rather than sitting blank, because a blank reads as zero to anything consuming the table. Service is sold only against a warranty in force, included or extended.
1.10.0 | 2026-08-27 | Capacity-first equipment picker on 2_Equipment. Pick a capacity — 60 kW, 120 kW, 360 kW, Level 2 and so on — and the SKU dropdown narrows to that capacity, five to fourteen SKUs instead of ninety-two. The capacity also supplies the rating kW where the price book records none, which it does for every Level 2, Buy America and V2G row; a Buy America 60 kW cabinet previously counted as zero kW and zero cabinets. A DC-only capacity line is added and the carbon credit repointed at it, because the LCFS credit is paid on DC capacity alone.
1.11.0 | 2026-08-27 | Distributed systems modelled properly. A power cabinet takes AC and produces DC and has NO connectors; a dispenser carries the connectors and no power of its own; an all-in-one is both in one enclosure. A Role column on 2_Equipment resolves from the SKU and decides whether a row contributes load, ports, both or neither, with DC output and AC input kept as separate figures — connected load now runs on AC input, so a 480 kW cabinet correctly draws 524 kW. 3_Electrical splits into AC runs (switchgear to cabinet or all-in-one) and a new DC runs block scheduling each dispenser back to its cabinet. Equipment architecture table added to PriceBook from the Chargetronix Nexus spec sheets.
1.12.0 | 2026-08-27 | Dispenser placeholder and hard limits on distributed systems. A cabinet row now carries a Dispensers-per-cabinet field, each assumed dual-port, for use until the dispenser SKU reaches the price book; dispensers entered as their own SKU are counted separately so the two routes cannot double-count. A distributed system is refused without dispensers, a dispenser is refused without a cabinet, and the count is capped at 3 dual dispensers for a 480 kW cabinet and 6 for a 1.28 MW. Forensic pass: computed columns no longer wear the fill-in styling, a stale community-choice-aggregator dropdown was removed from a computed cell, and the equipment table is cleared before rebuild so no value survives from an older layout.
1.12.1 | 2026-08-27 | Corrected the 1.28 MW power cabinet limit to EIGHT dual dispensers. Its published maximum is 16 connectors, so the dispenser cap is 16/2 = 8, not 6. The 480 kW cabinet is unchanged at 3 dual dispensers against its 6 DC outputs. Both limits are now the published connector maximum divided by two ports.
1.13.0 | 2026-08-27 | Dispensers can be priced by hand until their SKU reaches the price book. A Dispenser MSRP each column on the cabinet row feeds both the equipment MSRP and the after-discount line, at the same discount as the cabinet it sits on. A dispenser count entered with no unit cost is flagged rather than allowed to cost nothing.
1.14.0 | 2026-08-27 | Cabinet-to-dispenser runs are now costed the same way the switchgear-to-charger feeder is. Each DC run carries distance, circuits, engineer-chosen conductor, ground and conduit sizes, and whether it shares the AC trench; the sheet computes power conductor, ground, conduit, comms and trench footage and prices them at the RefData rates. Summary lines carry the DC material cost, trench feet and restoration area across to the Construction tab, with checks that every dispenser has a run and every run is sized. Also fixed: the design and engineering total on the Construction tab referenced the wrong three rows and returned $7,314 instead of $29,007.50.
2.0.0 | 2026-08-28 | Tabs renamed to drop the leading digit, which permanently removes the Excel quoting hazard. N() no longer wraps any range and every auto column returns 0 rather than a blank string — this was the cause of #VALUE! errors on four tabs. Utility and third-party fees are a standalone pass-through block, never marked up and never discounted. Discounts are set in one place and reach only work performed in house. Design and engineering billing rates live in cells.
2.1.0 | 2026-08-28 | Six changes made after 2.0.0 was released and shipped without the version moving, now recorded together. Tab-name references rewritten in prose and check messages. Michigan utilities added with their own picker column and the delivery-utility dropdown repointed at it. The retained-infrastructure register and the removal quantities are gated on project type, with a check that fires when removal scope is entered on a greenfield site. UMERC rate schedules added and the schedule list moved off-sheet to a range. The Fresno design ambient stripped: both ambients are now blank site inputs with no default. The market cross-check computes a steady-state projection on the Revenue tab and reads whichever revenue basis is in force, so it works on a greenfield site; the benchmark now names the market it is for and the verdict refuses to grade against the wrong one.
2.1.1 | 2026-08-28 | Presentation pass, no change to any value, formula or number format: column widths sized from the content actually in each column, row heights reflowed to match, frozen panes under the first heading, figures right-aligned and commentary indented, tabs coloured by what the sheet is for, and every sheet set to print landscape fitted to one page wide with a footer. The version moved for a formatting-only change because the content hash moved, and a hash that no longer matches its version is the failure this mechanism exists to prevent.
2.1.2 | 2026-08-28 | Removed a duplicate hash row this script had created by matching only the pre-rename label — two hashes for one workbook, inside the mechanism built to stop exactly that. Both scripts now accept either label.
2.2.0 | 2026-08-28 | California stops being the default. The utility context block resolves every utility in the picker, not only the Californian ones, and a new interconnection regime line says whether Rule 29 applies at all; the Electrical interconnection block is retitled, its Rule 29 rows marked CA ONLY, and the $3,500 PG&E design fee default removed — it had already followed a Michigan project into its cost build-up. The market benchmark table moves to RefData and the intake looks the figure up from the state chosen on the Revenue tab instead of carrying California typed in two more places, and that state now has no default. The time-of-use shares are blank rather than a remembered 4-9 pm peak, with a check that a partial split is not read as a complete one. New tariff provenance block: where the rate figures came from, whether anyone verified them against the filed sheets, and the demand-schedule eligibility threshold the Van Riper proposal had to state without a cell behind it. Changelog rows sorted and the two returning-instruction bullets moved out of the table the release script walks.
2.5.0 | 2026-08-28 | Connector counts come from the price book, per SKU, and the Equipment tab stops guessing. The auto column ended in IF(capacity="Level 2 AC",2,2) — the same answer in both arms of the test — so every SKU outside the five-row architecture table counted as two connectors: 93 of 98 SKUs, every single-port Level 2 and every single-connector DC unit. Ports drive the network fee, the port-expansion multiple and the whole utilisation projection, so the error ran through everything downstream. New CONNECTORS column on the price book with a second column recording how each count was decided, the formula reads it, and a scheduled SKU with no count returns 0 and fires an entry check rather than defaulting to a plausible wrong number. Redding Electric Utility added to the rate library with both commercial schedules and its DC fast charger rebate, and the rate-schedule cell finally points at the picker column that was built for it. The tariff now decomposes on the Revenue tab into volumetric, customer and demand charges with the billing demand stated, because a demand charge hidden inside a blended cents-per-kWh is how a fast-charging site gets priced into a loss. The rate-table scan moved to a defined name and the rebate block moved down to leave room for the next sixteen schedules. Gateway's 4,000 A main breaker note removed from the Overrides register. DISTRIBUTION EQUIPMENT SCHEDULE and LEVEL 2 BRANCH CIRCUITS added to the Electrical tab. The words disconnect, subpanel and panelboard appeared nowhere in this workbook as scope: it modelled one switchboard and branch runs straight from it to each charger, which was enough while every site was one voltage with one board. A two-voltage site had nowhere to put its service disconnect, its subpanels or its per-charger disconnects, so they would have arrived as one lump in the Overrides register with nothing able to check whether anything had been forgotten. The distribution schedule takes one row per item with what feeds it, what it feeds, who provides it and what it costs, and fires on any item with no source or no price. The Level 2 block exists because single-phase branch circuits off a panelboard are not three-phase feeders off a switchboard, and because the AC runs table holds twelve rows against a site with fourteen units. An NEC 625.43 advisory states the disconnect rule and both counts rather than deciding it. And load management is finally wired to something: Load management proposed? and Capped site draw sat on the Electrical tab and NOTHING read them, so the connected load, the design current, the required frame and the adequacy verdict all ran on full nameplate whatever the answer was — the one input that decides whether a site fits inside the service it already has was inert. The AC runs table gets the wire take-off the DC runs table has had since distributed systems were added: feet of phase conductor, the NEC 250.122 equipment ground and its feet, conduit, a comms run and a material cost per run, at RefData rates, with a block total. Until now the charger-side copper was priced in the PROJECT MODEL instead — run_material() in build_project.py — so the intake sized a conductor and something two artefacts away costed it, and nobody filling the sheet could see what a conductor change was worth. The 250.122 ground table moves out of the model into RefData so both read one table, marked UNVERIFIED because it was transcribed from the model rather than the printed NEC page. WIRE_AL added: RefData has carried an Aluminium $/ft column all along with no name pointing at it, so every take-off priced conductor at copper rates whatever the material said. Conduit size is now an entry on each AC run rather than a 4 inch assumption inside the model. A What this run feeds column names each line from its equipment role — all-in-one charger, power cabinet, or a dispenser that belongs in the DC block instead.
2.6.0 | 2026-08-28 | Limits a 4.2 MW site with 24 dispensers walked into, each one a boundary the workbook did not announce. The DC runs table held TWELVE rows against a site needing 27, so the runs were entered by copying rows past the end and the totals underneath went on summing the first twelve: $14,769 counted against $95,725 of conductor actually entered, a longest run reported as 77 ft when it was 129, and "every run sized and costed" reading OK with fifteen rows outside its range. The table is now 32 rows — four cabinets at eight dual dispensers, the architecture the table own maximum — every total and check is bound to the table extent, and a new check fires when a run names no cabinet. The block moved to the foot of the tab because twenty rows had to come from somewhere and openpyxl cannot insert without breaking absolute references. The service OCPD lookup returned #REF! on anything past 6,000 A instead of saying the device is off the end of the list, which poisoned the ampacity floor, the voltage drop and the verdict. The frame schedule jumped 5,000 to 10,000 A with no price above 5,000, so the sheet named a frame it could not cost; a 6,000 A row is added and the adequacy check now reports when the frame required has no price behind it. The Equipment tab dispenser check sat OUTSIDE the banner that sums the entry checks, so the tab read ERROR and ALL CHECKS PASS at once; the banner now covers it, ignores blank rows, and the check asks the right question — dispensers may be entered on their own line OR as a count on a cabinet row, and the fault is using both. Power cabinets are exempt from the connector-count check, because their connectors live on their dispensers. On a greenfield project the existing-service checks stand down instead of dividing by the "N/A" someone typed into a numeric cell and returning #VALUE!. Tap box, utility substation and meter/CT cabinet added to the distribution schedule types.
2.7.0 | 2026-08-28 | A service can be more than one board. The live electrical check took the whole site load, applied 125%, looked up ONE standard frame and asked whether the frame being priced covered it. Above about 4,000 A that is not how anyone builds: a 4.19 MW site is 6,303 A at 125%, past the largest frame RefData can price and past the largest device in the standard list, and the sheet had no answer but a 10,000 A frame it could not cost. The tab now asks how many boards are in the lineup and sizes each one — NEC 230.71 allows up to six service disconnects in separate enclosures — so 6,303 A becomes two boards at 3,151 A, both of them products RefData prices. The adequacy check reports per board and still says when the frame required has no price behind it.
2.7.1 | 2026-08-28 | The service feeder block still assumed one run. 2.7.0 taught the frame check that a service is a lineup rather than a board; the feeder block one section down went on taking the whole site load, applying 125% and asking for a single conductor, which on a two-board service reads 6,303 A and reports ABOVE THE LARGEST STANDARD DEVICE about a conductor that does not exist. It divides by the board count now. A run the serving utility provides under its EV infrastructure rule also stops asking us to pick a conductor for it — the field that says the utility provides it was already there and the verdict ignored it. And the market-benchmark row lost the percentage format it inherited from the utilisation cell beside it, which the stale-format check had been flagging correctly.
2.7.2 | 2026-08-28 | Presentation only — not one value, formula or number format changes. The formatting pass had three defects that the Electrical tab, now the longest in the book, made impossible to ignore. Long prose was measured for column width unless someone had remembered to mark it wrapped, so six columns were pinned to the 62-wide cap by single paragraphs and the sheet could not be read across; any string long enough to be a sentence is now wrapped before anything is measured. Widths were raised but never lowered — the label column could only grow and a note column took max(existing, want, 34) — so once anything had pushed a column wide it stayed wide forever; the row-height pass had learned that lesson and the width pass had not. And a paragraph sitting alone on its row was left inside one narrow column, eleven lines tall and clipped by the height cap, instead of spanning the empty cells beside it. Row heights are also computed from what a formula SHOWS, read from the cached result, rather than skipped: the run tables carried verdicts like "OK - 2,520 A against a 2,500 A floor" in eleven-point rows, overlapping the line below. The tallest row on the Electrical tab falls from 200 points to 80.
2.8.0 | 2026-08-29 | A 500 A disconnect rate joins the switchgear and breaker price block at $4,000, and the distribution schedule stops carrying typed prices. Every line whose cost basis reads RefData rate now computes quantity times a SUMIFS lookup on the price block — SUMIFS rather than a two-criteria INDEX/MATCH, because a two-criteria MATCH is an array formula in disguise and Excel resolves it by implicit intersection, which is the defect that shipped four broken revisions of this workbook. Three prices leave the build scripts as a result: the switchboards, the feeder breakers and the disconnects. Change a rate in RefData and every project that reads it follows, which is the whole reason RefData exists.
2.8.1 | 2026-08-29 | Excel was discarding a formula from this template and saying so only in a repair log. The NEC 625.43 advisory on the distribution schedule was written as one 346-character string constant and Excel refuses any constant over 255 — it does not shorten such a formula, it deletes it, so the check was simply absent from every copy a client opened. It is now built as concatenated chunks, and the verification suite enforces all three of Excel formula limits that LibreOffice does not: 255 characters in a constant, 8,192 in a formula, 64 levels of nesting. Separately, the twenty-nine rows left behind when 2.6.0 moved the dispenser run schedule to the foot of the Electrical tab are gone. They held no values, but they kept the header band, the striped fills, the merges and the row heights of the table that used to be there, so the tab carried what looked like a broken schedule between two working ones. A note now counts as prose at 55 characters rather than 120, which is the same threshold that decides to wrap it, and a sheet wider than twelve columns prints across the pages it needs instead of being squeezed onto one.
2.9.0 | 2026-08-29 | The demand subscription is computed. This template declared a subscription policy, supplied every input a ramp needs and left both outputs blank, so on a schedule that sells capacity in blocks the largest operating cost on a high-capacity site was not in the workbook at all. Expected peak concurrency and Subscribed kW are now derived from the day's energy, the peak-to-average factor and the safety margin; the block size and price are read from the rate library; and the annual cost joins the fixed-and-demand line the project model reads. Where the library carries no block for a schedule the cost is zero and the check says UNPRICED with the subscribed capacity in it, because a zero that nobody has priced is an absence and not a saving.
3.0.0 | 2026-09-01 | Consolidates the structural changes proved out on a full replacement-site engagement. THE DEMAND-LIMITING SETPOINT IS ITS OWN ROW on the electrical tab, separated from the sizing cap: the cap is read as the connected load and sizes conductors, gear and power per charging position, so typing a billing setpoint into it cuts the revenue projection to buy a demand-charge saving. THE PG&E AND CPUC BRANDING IS OUT of the interconnection block — eleven rows named PG&E, Rule 29, Rule 15, Rule 16 and the ITCC, none of which exists on a municipal utility; the concepts stay and the branding goes. REMOVAL CREW DAYS ARE INSIDE THE CREW DAYS, not added to them, with a check that the day count covers removal and installation both — the old label caused a model to add twelve removal days to a fifteen-day job. A PRICE POSITION row records what is being done about a guard-rail breach and what would release it. TWO ROWS THE MODEL ENGINE NOW READS: annual tariff escalation, because the engine held every tariff flat for ten years, and whether service is renewed after the contract, because the engine charges the uncovered years as an operating cost. The override register loses its Rule 15/16 label. KNOWN OPEN ITEM: the steady-state projection on the revenue tab still blends DC and Level 2 into one average kW while the model computes each stream on its own physics, so the model prints a reconciliation note naming the difference. Closing it needs derived DC and Level 2 position counts on the equipment tab as well. FIXES A CIRCULAR REFERENCE INTRODUCED AT 2.9.0: the demand-subscription block matched the rate library on cell B7, which holds a derived dollar figure, instead of B35, which holds the utility name. B7 depends on B95 depends on B102 depends on B100, which read B7 — a closed loop, and Excel warned about it on every open. The same wrong reference also made the block-size and block-price lookups compare a utility name against a dollar amount, so they returned zero for every project on a subscription tariff and the subscription cost nothing. No delivered model or proposal is affected: the block was new at 2.9.0 and no project workbook was ever built on it.
3.1.0 | 2026-09-03 | Presentation and ease of use. Nothing this workbook ASKS has changed — every label, formula and check is as it was at 3.0.0. ONE COLOUR NOW MEANS "TYPE HERE": pale blue, on all 771 cells that used to be yellow as well as the ones already blue, so a filler learns the convention once instead of twice. FORMULAS ARE LOCKED AND FIELDS ARE OPEN, with no password — typing over a derived cell used to destroy it silently, which is the same class of fault as a lookup pointing at the wrong cell. Unprotect the sheet in two clicks if you genuinely need to change one. THE ZOOM IS 100% ON EVERY TAB; it was 50, 90, 100 and 110, and the two tabs that open first were at 50. COLUMN A IS SIZED TO ITS OWN TAB rather than 44 everywhere, closing the dead gap between a label and its field. TAB COLOURS ARE A MAP: control teal, site and build purple, commercial green, overrides amber, reference grey. IT PRINTS — fit to width, length free to run, header row repeated on every page, print area set; a blank template was 71 pages. Row heights now fit the wrapped text that was being clipped mid-sentence, the AC-run table has one rhythm instead of a first row three times the others, stray Calibri cells are Arial, and nine closed questions gained the dropdown they were asking for. THE CHANGELOG ITSELF WAS BROKEN: the 3.0.0 entry had been written into the Released column with no date and no styling, so the most recent change to this template was the one page of it nobody could read. Both tail entries are back in the table, and the whole log is Arial 9 in a column wide enough to hold it instead of 11-point monospace clipped mid-word — the Version tab alone was ten of the fifty-five printed pages.

## README
EVSE PROJECT INTAKE
Zero Impact Energy — one form, one project. Fill the blue cells; everything else is derived.
How to use this workbook
• | Fill in every BLUE cell you can. Leave a cell blank rather than guessing — a blank is a question we will ask; a guess becomes a number in a proposal.
• | YELLOW cells are key commercial assumptions. They have sensible defaults, but they drive the return — change them deliberately, not by habit.
• | GREEN cells are live checks. They recalculate as you type. If a green cell turns into a warning, the sheet is telling you two of your inputs disagree.
• | GREY tabs (Lists, PriceBook, RefData) are reference data. Do not edit them unless prices have actually changed.
• | When the form is complete, send the file back. Everything downstream — electrical sizing, materials, labour, revenue, carbon, financing, the proposal — is computed from these inputs alone.
Cell legend
Appearance | Meaning | What to do
Blue fill, blue text | Human input | Fill it in
Yellow fill, blue bold | Key commercial assumption | Review the default, change deliberately
Green fill, green text | Live check / derived | Read it — never type over it
Grey | Reference data | Leave alone
Tabs, in the order you should fill them
1_Project | Who, where, which utility, and how the site is accessed
2_Equipment | What is being sold — pick SKUs from the price book
3_Electrical | Distances, wire, existing service. Drives every electrical cost.
4_Construction | Site works, labour days, ADA, permits, rentals
5_Commercial | Discounts, financing terms, service and network term
6_Revenue | Pricing, utilisation, ramp and growth
7_Carbon | FCI credit rate, aggregator, eligibility, grants
8_Deal_Structure | Optional. Knobs for trading price against a share of credits or revenue.
9_Overrides | Optional. Force any derived value when you have a quote or a measurement.
Version | Template 1.4.0, released 2026-08-26 — see the Version tab
Replacement projects
• | The Existing tab is the difference between a greenfield project and a charger swap. Complete it whenever the site already has charging equipment.
• | Set the project type on the Existing tab section A first — every other check on that tab keys off it.
• | Section B is the register that decides the cost. Marking the service, feeder, switchgear and conduit as RETAIN removes most of the electrical and civil scope; the Electrical and Construction tabs then tell you exactly which lines to zero.
• | Section E is the most valuable page in the whole intake. Twelve months of metered history beats every market assumption on the Revenue tab, and twenty-four months beats twelve. Enter outage months as they happened — do not smooth them.
• | Sections F and G turn the old installation into a projection: availability recovered, ports added, connector coverage widened and power increased, each with its own capture factor you can argue with.
• | Section H is the removal scope. It is zero on a greenfield project and real money on a replacement.
• | Set the revenue basis at the foot of the Revenue tab to "Historical actuals" on any replacement site with twelve or more months of data.
Choosing the utility
• | Pick the DELIVERY utility on the Project tab — the one that owns the wires and sets the tariff. If the site buys generation from a community choice aggregator, still pick the delivery utility; the CCA is a separate field below it.
• | A CCA changes only the generation cents per kWh. Eligibility, time-of-use periods, the demand subscription and every delivery charge stay with the utility. Build the bill from the delivery tariff and substitute one line.
• | Rule 29 exists only at investor-owned utilities. A municipal utility, irrigation district or cooperative has its own line-extension policy and the cost split can be completely different — do not carry a Rule 29 allowance on a POU site.
• | Read the STATUS column on RateLibrary before using any rate. VERIFIED means it was read in the utility's own tariff. NOT PUBLISHED means the utility does not publish it — SCE is the significant case — and those rows are left at zero deliberately rather than filled with a guess.
• | Whether a utility has an EV tariff at all is often worth more than the cents per kWh. A site on a utility with no EV rate pays full demand charges on a general commercial schedule, which at low utilisation dominates the bill.
Returning this workbook
• | Send the whole workbook back, not extracts. The version tab is how we know which generation of questions you answered.
• | If you are returning a file built on an older template, say so in Notes — some fields will have moved.

## Project
1 · PROJECT AND SITE
Identity, location, utility and access policy.
Client
Client legal name | Best Western Hawthorne | As it will appear on the proposal
Client contact name | Mohammad Noorali
Contact title | General Manager
Contact email | gm@example.com
Contact phone | 310-555-0100
Site
Site name | Best Western Hawthorne
Street address | 15000 Hawthorn Blvd
City / State / ZIP | Hawthorne, CA 90260
County | Los Angeles
Property type | Hotel | Retail, dealership, fleet depot, hotel, grocery…
Project type |  | Set this on the Existing tab. A replacement site must complete the Existing tab in full; a greenfield site leaves it blank.
Existing chargers on site? |  | Derived from the equipment schedule on the Existing tab.
Access and operating policy
Public access | Public 24/7 | Public 24/7 / Public during business hours / Restricted
Hours open per day | 24 | CRITICAL: 24 unless access is genuinely gated
Days open per year | 365 | Use 365 unless the site closes seasonally
Utility
Electric utility (delivery) | SCE — Southern California Edison | Pick from the list. This is the utility that DELIVERS power and therefore sets the EV tariff — see the Utilities tab. If the site is served by a community choice aggregator, still pick the delivery utility here.
Current rate schedule | TOU-GS-2 | From a recent bill
Existing service size (A) | 800 | Main service amperage today
Service voltage | 480 | Usually 480V 3-phase for DC fast charging
12 months of bills obtained? | Yes | Yes / No — needed to validate the energy cost
Commercial
Proposal date | 2026-09-01
Proposal validity (days) | 30
Prepared by | Vatsal Patel
RSM / account owner | Account Owner
Utility context — derived from the selection above
These read the Utilities and RateLibrary tabs. They tell you what tariff regime the site sits in before anyone opens a tariff book.
Utility type |  | IOU utilities are CPUC-regulated and follow Rule 29. POUs and co-ops set their own rules — no Rule 29, no PCIA, their own interconnection process.
Service territory
EV rate status |  | Whether this utility publishes a commercial EV tariff at all. Where it does not, the site pays full demand charges on a general commercial schedule — usually the single largest difference between two otherwise identical sites.
Rate rows in the library |  | How many schedules the library carries for this utility. Zero means it has not been researched — obtain the tariff.
Best status in the library |  | Never price a project from a NOT PUBLISHED row. Get the tariff sheet or a written rate quotation.
Community choice aggregator, if any | Clean Power Alliance | A CCA changes ONLY the generation $/kWh. Eligibility, time-of-use periods, the demand subscription and every delivery charge stay with the utility above.
CCA delivery utility check |  | Catches an aggregator paired with the wrong delivery utility. Central Coast Community Energy genuinely spans both PG&E and SCE, so it will flag — settle the host utility by address. Silent where no aggregator is named and outside California, where the mechanism does not exist.
Interconnection regime |  | Decides whether the Rule 29 questions on the Electrical tab are worth asking. Outside a California investor-owned utility they are not, and nothing reads them.
INTERCONNECTION IS THE SERVING UTILITY'S ANSWER, NOT OURS. California investor-owned utilities publish Electric Rule 29 and Rules 15/16, and the interconnection block on the Electrical tab can carry their allowances. Municipal and publicly owned utilities are not CPUC-regulated and generally publish no equivalent — there is no general substitute. Ask the utility what it requires and what it charges, and carry their figure as a pass-through fee. Do not price an interconnection from this template.
Note on B22: If you enter fewer than 24 hours, the carbon capacity credit must be recalculated — CARB computes the FCI capacity allowance against a 24-hour day. Restricted access reduces both revenue and credit.

## Existing
1B · EXISTING INSTALLATION — RIP AND REPLACE
Complete this tab only when the site already has charging equipment. On a greenfield site leave it blank and the model ignores it entirely. On a replacement site this tab is the most valuable page in the intake, because it replaces market assumptions with the site's own operating history.
A · Project type
Project type | Rip and replace — reuse infrastructure | Greenfield builds everything. Rip and replace swaps the chargers and reuses the electrical infrastructure. Replace and expand does both — new chargers plus added capacity.
Age of the existing installation (years) | 7 | Drives whether the existing conductors and gear are worth reusing.
Reason for replacement | End of life and unreliable | End of life, unreliability, obsolete connectors, insufficient power, or a commercial decision.
Who owns the existing equipment? | Client | If a third party owns it, removal and disposal need their agreement.
B · What is retained and what is replaced
This register is the whole commercial difference between a greenfield project and a replacement. Every line marked RETAIN removes cost from the electrical and construction scope. Every line marked REPLACE puts it back. Answer honestly — a conductor that is retained on paper and re-pulled in the field is a change order.
Element | Decision | Basis for the decision
Utility service and meter | RETAIN | Existing service stays. No Rule 29 application, no new meter.
Service feeder to switchgear | RETAIN | Conductor from the point of delivery to the switchboard.
Main distribution switchgear | REPLACE | Switchboard, main breaker and metering section.
Branch conductors to each charger | RETAIN | The feeders from switchgear to cabinet. The single largest reuse saving.
Conduit and trench | RETAIN | Existing conduit reused; no re-trenching if the new cabinets land on the same pads.
Branch breakers | REPLACE | Sized to the new cabinet, not the old one. Usually cheap and always worth replacing.
Concrete pads | REPLACE | New cabinets rarely match the old footprint or anchor pattern.
Bollards and equipment protection | REPLACE | Usually disturbed by pad removal.
Paving and striping | PARTIAL | Reinstatement around the new pads only.
ADA stalls and route | RETAIN | Reused if the layout is unchanged and still compliant.
Signage | REPLACE | Network branding, pricing and connector types all change.
Network and payment hardware | REPLACE | Integrated in the new cabinets.
Elements retained |  | Of 12 in the register.
Elements replaced
Scope profile |  |  | What the retained register implies for the electrical scope on the Electrical tab.
C · Existing equipment being removed
One row per existing cabinet or unit. This drives the demolition, disconnection and disposal scope on the Construction tab, and the port comparison in section F.
Make and model | Rating kW | Ports | Connectors | Qty | Year installed | Working?
ABB Terra 54 | 50 | 2 | CCS1 / CHAdeMO | 2 | 2018 | Working
ChargePoint Express 250 | 62.5 | 1 | CCS1 | 2 | 2019 | Failed
Existing units on site |  | Cabinets or standalone units to be removed.
Existing ports on site |  | Ports the site presents today.
Existing connected load (kW) |  | The load the existing service was sized for. Compare against the new load on the Electrical tab.
Units fully working |  | Quantity, not row count. The gap against units on site is the availability the new equipment recovers.
Units failed or intermittent |  | What the replacement is actually fixing.
Units of unknown condition |  | The availability uplift on the revenue projection is built from what was working and what was not. Anything in this row is a projection input nobody has established yet.
D · Existing electrical infrastructure
What is already in the ground. Where a line is being retained, this is what the new design has to work with; where it is being replaced, this is what has to come out.
Existing service size (A) | 800 | From the meter panel or the utility bill.
Existing service voltage | 480 | 480V three-phase for most DC sites.
Spare capacity in the existing gear (A) | 200 | What is available for the new equipment without an upgrade.
Existing switchgear frame (A) | 800 | The main breaker frame size.
Existing branch conductor size | 250 KCMIL Cu | e.g. 250 KCMIL Cu. Determines whether it can carry the new cabinet.
Average branch run length (ft) | 120 | Switchgear to cabinet, per position.
Existing conduit size and type | 2-1/2 in PVC | e.g. 2-1/2 in PVC. Determines whether a larger conductor could be pulled if needed.
Existing rate schedule | TOU-GS-2 | The tariff the site is billed on today.
Separately metered for EV today? | No | If not, a separate EV meter may be needed to reach the EV tariff.
Does the existing service carry the new load? |  |  | Stands down on a greenfield project, and asks for a NUMBER rather than a non-empty cell — "N/A" typed here used to reach a division and return #VALUE! on a site with no existing service at all.
Does the existing switchgear carry the new load? |  |  | Stands down on a greenfield project, and asks for a NUMBER rather than a non-empty cell — "N/A" typed here used to reach a division and return #VALUE! on a site with no existing service at all.
Load change from the existing installation |  |  | A replacement that raises connected load is the case where reuse assumptions break.
E · Historical usage and billing
Up to thirty-six months of actuals. This is what replaces the market benchmark on the Revenue tab. Enter what you have and leave the rest blank — the derived baseline below uses only the months that carry data. Where a month was an outage, mark it so it can be excluded from the run rate rather than dragging the average down.
Month (YYYY-MM) | kWh dispensed | Gross revenue | Sessions | Utility cost | Ports working | Note / outage
2025-09 | 9800 | 5390 | 306 | 2744 | 4
2025-10 | 10200 | 5610 | 319 | 2856 | 4
2025-11 | 9900 | 5445 | 309 | 2772 | 3 | Two units down all month
2025-12 | 11500 | 6325 | 359 | 3220 | 3
2026-01 | 12000 | 6600 | 375 | 3360 | 3
2026-02 | 11800 | 6490 | 369 | 3304 | 4
2026-03 | 12500 | 6875 | 391 | 3500 | 3
2026-04 | 13100 | 7205 | 409 | 3668 | 3
2026-05 | 12800 | 7040 | 400 | 3584 | 3
2026-06 | 13400 | 7370 | 419 | 3752 | 4
2026-07 | 13900 | 7645 | 434 | 3892 | 4
2026-08 | 14100 | 7755 | 441 | 3948 | 4
Months with data |  | Twelve is the minimum for a credible run rate; twenty-four is better.
Total kWh dispensed
Total gross revenue
Total sessions
Total utility cost
Average kWh per month
Average kWh per day |  | The historical daily run rate. This is the number the new projection is built from.
Historical kWh per year
Historical gross revenue per year
Historical utility cost per year
Historical net before card fees
Implied retail price $/kWh |  | What drivers actually paid. Compare against the price proposed on the Revenue tab.
Implied delivered cost $/kWh |  | What the utility actually charged, all-in. Far better than any tariff estimate.
Average kWh per session |  | Typically 25 to 55 kWh on DC. A low figure suggests failed or abandoned sessions.
Average ports working |  | Against the ports installed. The gap between them is the availability the new equipment recovers.
Historical availability |  | Ports working as a share of ports installed. This is the recovery opportunity, quantified.
OUTAGE MONTHS DRAG THE RUN RATE DOWN, AND THAT IS USUALLY THE POINT. A site that averaged 3.4 of 5 ports working was not meeting demand — it was rationing it. Do not "correct" the history upward. Enter it as it happened and let section F state the recovery separately, where a customer can see it and argue with it.
F · Port expansion and connector coverage
What the new equipment adds over the old. Each uplift below is stated separately so it can be challenged individually rather than hidden inside one optimistic growth rate.
Existing ports
New ports |  | From the Equipment tab. Dual-port cabinets present two positions each.
Port count multiple |  | More positions means more simultaneous vehicles, not proportionally more energy — see the capture factor below.
Connector | On the existing equipment | On the new equipment | Share of the California fleet
NACS / Tesla | No | Yes | 55%
CCS1 | Yes | Yes | 40%
CHAdeMO | Yes | No | 3%
J1772 (Level 2) | No | Yes | 2%
Enter the share of the local fleet each connector reaches. Tesla vehicles are the largest single population in California, so a site that could not serve them natively was turning away a large share of passing demand.
Fleet coverage today |  | Share of the fleet the existing connectors serve natively.
Fleet coverage after replacement
Coverage multiple |  | Adding NACS to a CCS-only site is the single largest addressable-market change available on a replacement project.
Existing power per position (kW) |  | DC positions only. Blending Level 2 into this average understates the old power and inflates the uplift.
New power per position (kW)
Power multiple |  | Capped at 2.00x. Faster charging frees the stall sooner, but beyond roughly double the constraint stops being how fast the hardware charges and becomes how many vehicles arrive. Raising the cap does not make demand appear.
G · Projected baseline — history plus stated uplifts
Four uplifts, each entered as a capture factor rather than taken at face value. A capture factor of 100% would claim the site converts the whole theoretical gain into energy sold; anything near that is not credible. The defaults below are deliberately conservative and every one of them is a blue cell you can argue with.
Historical kWh per year |  | From section E. The starting point.
Uplift | Theoretical multiple | Capture factor | Applied multiple | Basis
Availability recovered |  | 85% |  | Ports that were dark now work. The most defensible uplift on the list — the demand was already there and was turned away.
Ports added |  | 40% |  | More positions capture more simultaneous arrivals, but a second position does not double demand — it shortens the queue.
Connector coverage widened |  | 50% |  | Vehicles that could not charge here now can. Capture is below one because some of those drivers were already served nearby.
Higher delivered power |  | 25% |  | Faster sessions free the stall sooner. Only converts to energy where demand is waiting for a stall.
Combined uplift multiple |  | The four applied multiples compounded. Sense-check it against the site factor on the Revenue tab.
Projected kWh per year at steady state |  | History times the combined uplift. This is what the Revenue tab should use instead of the market benchmark.
Projected kWh per day
Sanity check against capacity |  |  | Stops an optimistic stack of uplifts producing a number the hardware cannot physically deliver.
Projection against history
Cross-check against the market
The capacity check above asks whether the hardware could physically deliver the projection. This asks whether the market would. Both have to pass, and the market one is usually the binding constraint.
Implied port-time utilisation |  | Share of the day each position delivers energy, at whichever projection is in force — history where history exists, the greenfield basis otherwise.
Benchmark port utilisation |  | Looked up from the market chosen on the Revenue tab. Zero means no market was chosen, or the one chosen is not in the table — and the verdict below says so rather than grading against nothing.
Projection as a share of the state average |  | Above 100% means the projection assumes this site beats the average Californian port.
Market plausibility |  |  | A replacement can transform a site, but it cannot make it beat the market without a reason you can name.
Market the benchmark is for |  | Reads the Revenue tab. It is not a second place to type a market.
THIS BASELINE REPLACES THE MARKET BENCHMARK, IT DOES NOT ADD TO IT. On a replacement site set the revenue basis on the Revenue tab to "Historical actuals" and the model will use the figure above. Leaving it on "Market benchmark" and entering history here will not double-count, but it will ignore the better data.
H · Removal, disposal and site protection
What it costs to take the old installation out. This is real scope on a replacement project and zero on a greenfield one.
Item | Quantity | Note
Cabinets to disconnect and remove (ea) | 4 | Includes de-energising, lockout and terminations
Concrete pads to break out (ea) | 4 | Saw-cut, break, remove and dispose
Bollards to remove (ea) | 8
Signage to remove (ea) | 4
Disposal loads (ea) | 2 | Concrete and steel to a licensed facility
Equipment recycling or resale? | Yes | Working units may carry salvage value
Hazardous material identified? | No | Older units may contain fluids requiring special handling
Temporary charging required during works? | No | If the site cannot go dark, this is a separate cost
Site protection and traffic control (days) | 5 | Barriers, cones and signage around a live customer lot
• | Removal, disposal and pad replacement are entered on the Construction tab as quantities like any other construction line. This section is where the quantities come from.
• | A site that must keep charging during the works needs a phased programme and possibly temporary units. That is not in the standard scope and should be priced separately.
• | Working units removed from service can carry salvage value. Where the client wants that credited, it belongs on the Overrides tab as an override, not buried in the construction estimate.

## Equipment
2 · EQUIPMENT SCHEDULE
Pick the CAPACITY first, then the SKU. A distributed system is TWO kinds of line: the power cabinet, and each dispenser it feeds.
Enter one row per SKU. Qty is the number of CABINETS, not ports.
Line | Capacity | SKU | Description (auto) | Role (auto) | DC output kW (auto) | AC input kW (auto) | Connectors (auto) | Qty (units) | Discount — set on the Commercial tab | MSRP each (auto) | Dispenser SKU (distributed only) | Max dispensers (auto) | Dispensers per cabinet | Connectors per dispenser (1 or 2) | Dispenser MSRP each (auto)
1 | 360 kW DC | TP5-360-480-2-300 | [5 empty] | 4
2 | Level 2 AC | CTX-C40-240-2 | [5 empty] | 2
3
4
5
6
7
8
9
10
11
12
Charging units (excludes accessories) |  | Units a driver plugs into — dispensers, all-in-one chargers and Level 2. A power cabinet has no connectors and is not one.
AC-connected units — cabinets and all-in-ones |  | Each of these needs its own AC run from the switchgear, and a placement distance on the Electrical tab.
Total ports |  | Connectors x units. The EVOLV billing basis. Dispensers carry the ports on a distributed system; the cabinet carries none.
Total connected load (kW) |  | AC input, which is what the switchgear sees — a 480 kW cabinet draws 524 kW. Dispensers add nothing: their power comes from the cabinet, not the switchgear.
Equipment MSRP total |  | Catalogue SKUs at their price-book price, plus any dispensers priced by hand on the cabinet row.
Equipment after discount |  | Sales tax is computed on THIS, not on MSRP. The discount is the one on the Commercial tab — there is no per-line discount any more.
of which DC fast-charging capacity (kW) |  | DC output. The LCFS credit basis. Counted once, at the cabinet — never again at the dispenser.
Scope of work sentence (one line, must match the rows above) | Installation of (4) 360 kW dual-port DC fast chargers and (2) dual Level 2 units — 12 charging positions
Write it from the table, e.g. "Installation of (4) 360 kW dual-port DC fast chargers — 8 charging positions".
Distributed system — do the dispensers fit the cabinets?
Only relevant when a power cabinet is on the schedule. A cabinet feeds a limited number of DC outputs; each dual dispenser consumes two of them. Every dispenser also needs a DC run back to its cabinet — schedule those on the Electrical tab.
Power cabinets on site
Dispensers those cabinets can take |  | From the architecture table: a 480 kW cabinet takes up to 3 dual dispensers, a 1.28 MW up to 8.
Dispensers on the cabinet rows |  | Dispensers per cabinet x the number of cabinets. This is now the only way a dispenser is entered.
Dispensers entered on a line of their own |  | Should always be zero. A dispenser belongs on its cabinet row, not on a line of its own.
Dispensers in total
Connectors those dispensers carry
DISTRIBUTED SYSTEM CHECK
Dispenser value at list |  | Dispensers x their price-book price. Included in the two equipment totals above.
Is a dispenser SKU picked where dispensers are scheduled?
Any dispenser on a line of its own? |  | It used to fire whenever a dispenser was on its own line at all, which is a legitimate entry now the dispenser SKU is in the price book. The thing that is actually wrong is using both routes, because the totals sum them.
ENTRY CHECKS — what a wrong entry looks like
Each of these is a real way to get a wrong answer out of this tab. None of them used to say anything.
Any discount typed on an equipment line?
Dispensers counted twice?
Anything entered below the table?
Every SKU found in the price book?
Every line with a SKU has a quantity?
Every line with a capacity has a SKU?
Every SKU has a connector count? |  | Power cabinets are exempt: their connectors are on their dispensers, which are scheduled separately. Accessories are exempt for the same reason — they are not charging positions.

## Electrical
3 · SITE AND ELECTRICAL
Distances and materials. This tab drives the largest single cost in the project.
Materials |  |  |  | Conductor sizing basis
Feeder conductor material | Cu | Cu or Al |  | Design ambient (C) | 40 | Design ambient for the branch runs, in Celsius. THIS IS SITE DATA — there is no house default and none is offered. Use the ASHRAE 2% design dry-bulb for the location, or the duct-bank design temperature if the run is buried. NEC Table 310.15(B)(1)(1) corrects the ampacity from it, so an ambient carried over from another project silently resizes every conductor on this one.
Conduit type | PVC | PVC or EMT |  | Conductor insulation rating (C) | 90 | What the wire is rated for. THHN/XHHW-2 is 90 C. Ambient correction is applied to THIS column.
Trench surface | Asphalt | Asphalt / concrete / landscape / mixed |  | Termination rating (C) | 75 | NEC 110.14(C). The corrected ampacity is capped here. Confirm against the switchgear and the cabinet terminals — 60 C lugs change every size on this tab.
Trench depth (in) | 24 |  |  | Allowable voltage drop (%) | 3% | NEC treats voltage drop as an informational note, not a requirement. On a 300 ft feeder it is usually what decides the size.
AC runs — switchgear to each charger: all-in-one units and power cabinets alike |  | One feeder per AC-connected unit. An all-in-one charger and a power cabinet both take a feeder and both belong here; a DISPENSER does not — it takes DC from its cabinet and is scheduled in the DC runs block further down. The "What this run feeds" column below says which is which for every line.
Unit | Equip. line | AC input kW (auto) | Distance from switchgear (ft) | Design current A (auto) | Continuous 125% A (auto) | OCPD A (auto) | Ampacity floor A (auto) | Conductor size | Sets in parallel | Ampacity per set, corrected (auto) | Provided A (auto) | Voltage drop % (auto) | Verdict (auto) | Conduit size | What this run feeds (auto) | Phase conductor (ft) (auto) | Ground size (auto, 250.122) | Ground (ft) (auto) | Conduit (ft) (auto) | Comms (ft) (auto) | Material cost (auto)
Charger 1 | 1 |  | 80 |  |  |  |  | 300 kcmil | 2 |  |  |  |  | 3"
Charger 2 | 1 |  | 95 |  |  |  |  | 300 kcmil | 2 |  |  |  |  | 3"
Charger 3 | 1 |  | 110 |  |  |  |  | 300 kcmil | 2 |  |  |  |  | 3"
Charger 4 | 1 |  | 125 |  |  |  |  | 300 kcmil | 2 |  |  |  |  | 3"
Charger 5
Charger 6
Charger 7
Charger 8
Charger 9
Charger 10
Charger 11
Charger 12
AC branch material cost ($) |  | Phase conductor, equipment ground, conduit and a comms run for every AC branch, at RefData rates. This used to be computed in the project model instead, so a conductor size could be changed here and the cost only moved two artefacts later. The model now reads this figure.
Total AC branch distance (ft) |  | Switchgear to the cabinets only. The transformer-to-switchgear run is separate and is sized in its own block at the foot of this tab.
AC-connected units placed |  | Must equal Total cabinets on 2_Equipment
Placement matches equipment? |  | Counts power cabinets and all-in-one chargers. Dispensers are not counted here.
Every AC run costed?
Service and switchgear
Point of connection | Existing MSB | Existing MSB / new service / pole transformer
Distance, transformer to switchgear (ft) | 40 | Customer-side feeder, our scope. Sized in the service feeder block at the foot of this tab, which has its own material and its own ambient.
Distance, switchgear to pole (ft) | 120
Spare capacity in existing gear (A) | 200 | 0 if a new service is required
Load management proposed? | No | Yes caps site draw below full nameplate
Capped site draw (kW) if load managed |  | SIZING CAP — conductors, gear and the service are sized on this, and it drives power per charging position in the model. Leave blank if not load managed. It is NOT the billing setpoint: that is its own row below, and the two are different numbers.
Service boards in the lineup | 1 | One unless the service is split. Above roughly 4,000 A it usually is: NEC 230.71 allows up to six service disconnects in separate enclosures, and the frame below is sized PER BOARD. A site needing 6,303 A has no single frame RefData can price; two boards at 3,151 A each have one.
Live electrical check — derived from 2_Equipment
Connected load (kW) |  | Full nameplate from the equipment schedule, or the managed cap when load management is proposed and a cap is entered. Sizing to a managed maximum needs an energy management system under NEC 750 and the engineer's sign-off — the sheet applies the cap you enter, it does not certify it.
Design current at service voltage (A) |  | kW x 1000 / (V x sqrt 3)
Required OCPD at 125% (A) |  | NEC continuous-load rule
Standard frame required per board (A) |  | The required overcurrent device divided across the boards in the lineup, then rounded up to the next standard frame.
Switchgear size being priced (A) | 3200 | Type what you are actually quoting
Switchgear adequate? |  | Checks the per-board size AND whether the workbook can price that frame.
Load management stated and capped?
Demand-limiting setpoint (kW) |  | BILLING SETPOINT, NOT A SIZING CAP. What the energy management system holds the highest fifteen-minute site draw to — which is what a demand charge is billed on. Nothing is sized on it. Leave blank and the model falls back to the sizing cap above. On a demand tariff this is usually the largest controllable line on the electricity bill; on a subscription tariff it is what you are buying blocks against.
Utility interconnection — governed by the serving utility
These rows are the SERVING UTILITY's answer, not ours, and they are written to suit any utility. Where the utility publishes an interconnection rule with an allowance — California investor-owned utilities do, under Electric Rule 29 and Rules 15/16 — record its figures here. A municipal or publicly owned utility usually publishes no allowance and no tax gross-up at all, in which case zero is a FINDING and not a gap, and the utility's own quote is the only number that belongs in the price.
Service type | Added load to existing service | New service / added load to existing service
Overhead or underground service | Underground
Distance to the utility point of interconnection (ft) | 150 | Drives whether distribution work is likely
Interconnection application submitted? | No | Yes / No — with date
Utility project or design number |  | Once issued
Utility interconnection design and application fee | 3500 | What the serving utility charges to design and connect the service. Leave blank until they say. There is no default: the $3,500 that used to sit here was PG&E's typical Rule 29 figure and it followed a Michigan project into its cost build-up.
Distribution or line extension indicated by the utility? | Unknown — design not yet submitted | Unknown until the utility design is returned
Line-extension allowance calculated by the utility |  | Leave blank until the design comes back. Municipal utilities often publish no allowance at all — zero is then a finding, not a gap.
Customer contribution above the allowance |  | Leave blank until the design comes back
Temporary or speculative service component? | Unknown | Temporary or speculative service only
Tax gross-up on a customer contribution applies? | Only if Rule 15/16 contribution arises | Tax on any contribution to utility-owned plant. Investor-owned utilities levy it; publicly owned utilities generally do not.
Transformer pad location agreed with client? | Yes | Client must provide the space
Proof of commitment to purchase provided? | Yes | Some utility programmes require a PO, budget approval or grant agreement
Client accepts the utility's operate-and-maintain obligation? | Yes | Where the utility imposes one as a condition of an incentive or an extension
Client accepts the utility's activation deadline after energisation? | Yes | Where the utility sets one
Utility design submitted (date)
Utility design returned (date)
Retained infrastructure — replacement sites only
Mirrors the register on the Existing tab section B. Where an element is retained, the corresponding material take-off should be entered as zero rather than left at the standard build quantity. These checks say plainly which lines to zero. ON A GREENFIELD PROJECT THIS WHOLE BLOCK IS INERT and says so — the register can hold whatever it likes and none of it reaches the take-off.
Project type |  | From the Existing tab.
Electrical element | Decision | What it means for the take-off
Utility service and meter
Service feeder
Switchgear
Branch conductors
Conduit and trench
Branch breakers
Electrical scope profile |  |  | The one-line summary of what the electrical estimate should contain.
Reuse feasibility |  |  | Repeats the Existing tab capacity test here, where the electrical estimate is actually built.
DC runs — moved to the foot of this tab
MOVED. The dispenser run schedule is now at row 171 of this tab, where it has 32 rows instead of 12 and totals bound to the table. It moved because a site with three 1.28 MW cabinets needs 24 rows, and the twelve-row table was extended by hand while the totals underneath went on summing the first twelve.
SERVICE FEEDER — TRANSFORMER TO SWITCHGEAR
One feeder carrying the whole site, so the load is the equipment tab's total rather than any single unit. The columns line up with the AC branch table above — load, distance, current, device, floor, size, sets, verdict all sit in the same columns — so the two tables can be read against each other. The distance is read from the Service and switchgear block above; do not retype it here.
Governing rule | Service conductor — NEC 230.42 | A conductor from the utility transformer to the service disconnect is a SERVICE conductor. Its overcurrent device sits at the far end, in the switchgear, so NEC 240.4(C) — which sizes a conductor to the device feeding it — does not apply. 230.42(A) asks for 125% of the continuous load, which is the same figure the branch runs start from but without the step up to the next standard device. Switch to Feeder if the run is protected at its supply end.
Who provides this run? | Utility — EV infrastructure rule | Under the California IOUs' EV infrastructure rules — PG&E Electric Rule 29, SDG&E Rule 45 and their equivalents — the utility designs, builds and owns the service from its transformer to the customer's service equipment. On those projects this run is NOT ours to price, and the bid excludes it by name rather than carrying it silently. It is still sized here, because we have to coordinate with what the utility installs and check it carries the load. Switch to Zero Impact Energy where the service point sits at the transformer secondary and the conductors are genuinely customer-side.
Design ambient for this run (C) |  | Site data for THIS run. A buried duct bank and a run on a south wall are different numbers, and neither is a house default.
Run | Conductor material | Site load kW (auto) | Distance to switchgear (ft) | Design current A (auto) | Continuous 125% A (auto) | OCPD A (auto) | Ampacity floor A (auto) | Conductor size | Sets in parallel | Ampacity per set, corrected (auto) | Provided A (auto) | Voltage drop % (auto) | Verdict (auto) | Per lateral. A two-board service has two of these runs, and asking one conductor to carry 6,303 A was a question with no answer.
Transformer to switchgear | [13 empty] | Stands down when the utility provides the run. It used to say "pick a conductor size" about a conductor that is not in our scope.
The branch runs above take their conductor material from the Materials block and their ambient from the sizing basis beside it. This run takes both from the two blue cells at the top of this block, because a long buried aluminium service feeding short copper branches is an ordinary design and the sheet should let you say so. Whatever is picked here is what the bid prices — the model no longer chooses.
DISTRIBUTION EQUIPMENT SCHEDULE
Every board, panel, disconnect and transformer between the point of connection and the chargers. Until this block existed the workbook modelled one switchboard and nothing else, so a two-voltage site had nowhere to put its subpanels and they arrived as one lump in the Overrides register. Price each line or say who does: an unpriced row in a schedule reads as free.
Item | Type | Qty | Volts | Phases | Rating (A) | Fed from | What it feeds | Location | Who provides | Cost basis | Quoted cost ($)
EVSE disconnects | EVSE disconnect | 4 | 480 | 3 | 600 | MSB | TP5 cabinets | Pad | Zero Impact Energy | Vendor quote | 12000
Distribution units scheduled
Distribution equipment cost ($) |  | Carried into the cost build-up as distribution equipment, at the materials markup. Enter it in the Overrides register if a single vendor quote covers the whole schedule.
Every item priced?
Every item fed from something?
EVSE disconnecting means — NEC 625.43
LEVEL 2 BRANCH CIRCUITS
Level 2 units are single-phase branch circuits off a panelboard, not three-phase feeders off a switchboard, and the AC runs table above cannot express them — it also holds only twelve rows, which a site with four DC units and ten Level 2 exceeds. Ampacity is read from the same RefData table and corrected at the same design ambient.
Circuit | Equip. line | Units on circuit | Volts | Amps per unit | Continuous 125% A (auto) | Breaker (A) | Distance (ft) | Conductor size | Ampacity (auto) | Verdict (auto)
L2-01 | 2 | 1 | 208 | 40 |  |  | 60 | 8 AWG
L2-02 | 2 | 1 | 208 | 40 |  |  | 75 | 8 AWG
L2-03
L2-04
L2-05
L2-06
L2-07
L2-08
L2-09
L2-10
L2-11
L2-12
L2-13
L2-14
L2-15
L2-16
Level 2 circuits scheduled |  | Units, not rows — a circuit can carry more than one unit where the panel schedule allows it.
Total Level 2 branch distance (ft)
Level 2 units placed against the schedule
DC runs — power cabinet to dispenser
One row per dispenser, cabinet to dispenser, priced exactly the way the AC feeder is. THIRTY-TWO ROWS: four 1.28 MW cabinets at eight dual dispensers each is the architecture table's own maximum. The totals below are bound to this table, so if it is ever extended again they follow. The block sits here rather than above the service feeder because twenty rows had to come from somewhere and inserting them would have broken every absolute reference in the workbook.
Dispenser | Fed from cabinet (line) | Distance (ft) | DC circuits | Conductor size | Ground size | Conduit size | Trench shared with the AC run? | Power conductor (ft) | Ground (ft) | Conduit (ft) | Comms conduit (ft) | Trench (ft) | Material cost
Dispenser 1
Dispenser 2
Dispenser 3
Dispenser 4
Dispenser 5
Dispenser 6
Dispenser 7
Dispenser 8
Dispenser 9
Dispenser 10
Dispenser 11
Dispenser 12
Dispenser 13
Dispenser 14
Dispenser 15
Dispenser 16
Dispenser 17
Dispenser 18
Dispenser 19
Dispenser 20
Dispenser 21
Dispenser 22
Dispenser 23
Dispenser 24
Dispenser 25
Dispenser 26
Dispenser 27
Dispenser 28
Dispenser 29
Dispenser 30
Dispenser 31
Dispenser 32
TOTAL
DC material cost |  | Conductor, ground, conduit and comms for every cabinet-to-dispenser run. Bound to the table above, all 32 rows of it.
DC trench to cut (ft) |  | Excludes runs sharing the AC trench.
DC trench restoration (sq ft) |  | Trench feet times the trench width implied by the depth entry above.
Total DC run distance (ft)
Dispensers placed
Placement matches the schedule?
Longest DC run (ft) |  | The binding constraint on voltage drop. It reads the whole table — it used to read the first twelve rows and reported 77 ft on a site whose longest run was 129 ft.
Every run sized and costed?
Every run assigned to a cabinet? |  | New in 2.6.0. Twenty-four dispensers arrived with this column blank on every row.
Note on B34: If Yes, confirm with the aggregator that capacity credits are still earned on full nameplate before relying on the carbon revenue.
Note on A41: This is the number that must agree with the switchgear you price. If the costed gear is smaller than this, the estimate is wrong.
Note on B56: Under Rule 29 PG&E pays for the design, engineering, trenching, conduit, transformer and metering of the EV service extension. The customer bears this design fee, the applicant-side equipment, and any Rule 15/16 contribution.
Note on B57: If PG&E must extend or reinforce distribution, a Rule 15 allowance is calculated and any excess becomes a customer contribution. It cannot be established until the utility design is submitted and returned. Exclude it by name until then.

## Construction
4 · CONSTRUCTION SCOPE
Site works and labour. Defaults come from the standard build; override where the site differs.
Labour
Crew days on site | 34 | Must match the construction schedule you publish
Crew day rate | 2750 | Fully burdened
Contingency on labour | 10%
Markup on labour | 20% | House standing decision: 20%, applied after contingency. Change it per project on purpose, not by inheriting the last one.
Labour total |  | Days x rate x (1 + contingency) x (1 + markup)
Construction PM as % of labour | 15%
Site works — enter quantities, leave blank to use the standard build
Item | Quantity | Unit basis | Unit cost | Include?
Concrete (yd3) | 6 | Pads per cabinet | 193.54 | Y
Rebar (ea) |  | 3 per cabinet | 25.65 | Y
Steel mesh roll (ea) |  |  | 169 | Y
Asphalt / paving (sq ft) | 400 | Trench restoration — $15/sq ft set by ZIE, 28 Aug 2026 | 15 | Y
Striping (lot) |  |  | 1500 | Y
ADA stalls (ea) | 2 | 2% of stalls, min 1 | 4900 | Y
ADA ramp (ea) | 1 |  | 5200 | Y
Bollards (ea) | 12 | 4 per DC cabinet / 2 + 6 | 110 | Y
Signs (ea) |  | 2 per DC cabinet | 40 | Y
Sign posts (ea) |  |  | 56.1 | Y
Switchgear sign (ea) |  |  | 150 | Y
GPR scan (ea) | 1 | Underground utility locate | 2500 | Y
GFI test (ea) | 1 | Required above 1000 sq ft gear area | 3500 | Y
Dump / disposal (lot) | 1 | Freight and disposal | 5000 | Y
Design and engineering
AutoCAD design — drawing sets | 3 | One issued drawing package: site plan, equipment layout, civil details. | 3412.5
Electrical engineering — drawing sets | 3 | One stamped electrical package: single-line, panel schedule, load calculation. | 2080
Project management — hours | 35 | Billed hourly across design, permitting and construction. | 358
Design and engineering total |  | Quantity in column B times the rate in column D. These are ZIE billing rates for work performed in house — change the rate here, not in a formula.
Equipment rentals — standard build, override durations if the job differs
Rental | Qty | Unit cost | Days | Include?
Fencing |  | 0.3 |  | Y
Mini x | 1 | 98.5667 | 30 | Y
Dump Truck | 1 | 520 | 4 | Y
Forklift |  | 563 |  | Y
Trench Plates |  | 5.18 |  | Y
Storage container |  | 185 |  | Y
Portable restroom |  | 267 |  | Y
Low boi |  | 1000 |  | Y
Saw cutter |  | 169 |  | Y
Jack hammer |  | 155 |  | Y
Compactor |  | 175 |  | Y
Generator rental | 1 | 220 | 10 | Y
Dump trailer rental |  | 796.63 |  | Y
Equipment protection |  | 45 |  | Y
Removal and demolition — replacement sites only
Zero on a greenfield site. On a replacement site these quantities come from the Existing tab section H and are priced like any other construction line.
Item | Quantity | Source
Cabinets to disconnect and remove (ea) |  | The Existing tab section H
Concrete pads to break out (ea) |  | The Existing tab section H
Bollards to remove (ea) |  | The Existing tab section H
Signage to remove (ea) |  | The Existing tab section H
Disposal loads (ea) |  | The Existing tab section H
Site protection and traffic control (days) |  | The Existing tab section H
Removal crew days — INSIDE the crew days above |  | ADVISORY ONLY. Removal overlaps the installation and is NEVER added to the crew days on the schedule above — a model that added them inflated labour by twelve days on a fifteen-day job. Use it to check the day count covers both.
Do the crew days leave room for the installation? |  | Removal is inside the crew days, so the crew days have to be big enough for the removal AND the installation.
Construction scope profile
Does the site stay live during the works?
Removal scope on a greenfield project?
A CHARGER SWAP IS NOT A SMALL GREENFIELD PROJECT. Demolition, disposal, working around a live customer lot and phasing to keep the site trading are real costs that a greenfield estimate does not contain. Enter them rather than assuming the reuse saving covers them.
MARKUPS — WHAT TURNS COST INTO PRICE
Markup on materials | 20% | Applies to switchgear, conductor, conduit, site works and construction rentals — everything priced from a rate rather than from a crew day. Set at 20%, matching the house markup on labour cost.
Markup on labour |  | Shown here for comparison only — the labour markup is still entered in the Labour block at the top of this tab. One input, one place.
Every materials rate in this workbook is a COST rate — the RefData switchgear table is headed "Cost", and the site-works unit costs are what the item costs to buy and place. Nothing turns them into a price. The note beside the labour markup at the top of this tab already says materials are marked up "the same way"; until this cell carries a figure, that is not true and the discount on the Commercial tab comes straight out of margin.
UTILITY AND THIRD-PARTY FEES — PASS-THROUGH
These are charges levied by someone else: the AHJ, the utility, the fire district. ZIE pays them and bills them on at exactly what they cost. They carry NO markup and NO discount, and they are shown as their own line on the bid — a fee schedule is a public document and a marked-up permit is the fastest way to lose an argument you should never have been having.
Fee | Quantity | Basis | Unit cost | Include?
Permit and plan-check fees | 1 | AHJ — verify locally | 4000 | Y
Utility contract fees | 1 | Application and contract | 3500 | Y
Utility interconnection design and application fee | 1 | Entered on the Electrical tab — this row reads it. Pass-through at cost. |  | Y
Utility line-extension contribution, if any | 0 | Whatever the serving utility charges the customer toward extending distribution or service. Zero until they say otherwise. |  | Y
Fire department plan review | 1 | Fire district — common on DCFC sites | 850 | Y
Encroachment / street-opening permit | 0 | Municipal, when trenching leaves the property | 0 | Y
Electrical inspection fees | 0 | AHJ inspection, separate from plan check | 0 | Y
Meter and service connection fee | 0 | Utility, if charged separately from Rule 29 | 0 | Y
Utility and third-party fees total |  | Billed to the client at exactly this figure. No markup, no discount, its own line on the bid.
Any fee left in the site-works table?
Note on B8: Without this, labour is billed at cost plus contingency and the builder earns only what contingency it does not spend.

## Commercial
5 · COMMERCIAL TERMS
Discounts, financing and the service and network term.
Discounts applied to customer price
Charger hardware discount | 7%
Service and warranty discount | 7%
EVOLV and commissioning discount | 0%
Labour and in-house services discount | 7% | Applies ONLY to work ZIE performs: construction labour, construction project management, and design and engineering. It may never be applied to materials, to equipment rentals, or to any third-party or utility fee.
Sales tax rate | 7.25% | Applied to the DISCOUNTED equipment price
Service, warranty and network
Contract length (years) | 5 | Years of service included in the price
In-warranty years | 2 | Years billed at the in-warranty rate
EVOLV network fee per port per month | 39.99
EVOLV annual cost |  | Ports x rate x 12 — ports, never cabinets
EVOLV cost across contract
Renew service after the contract? | Yes | Yes / No. The model measures the return over a longer horizon than the contract covers and charges the uncovered years as an operating cost. THE PLATFORM IS CHARGED EITHER WAY — without the network there is no session authorisation, no payment processing and no revenue. This row decides only whether service and extended warranty are renewed alongside it.
Financing
Financing offered? | Yes
Lender | De Lage Landen
Annual interest rate | 8.39%
Term (years) | 5
Payments per year | 12
Down payment | 0
Financing start date | 2026-10-01
Analysis horizon
Model horizon (years) | 10 | Use 10 — the carbon credit runs ten years
Discount rate for NPV | 8.39% | Default: the financing rate
Note on B28: A five-year horizon truncates the FCI credit at half its life and understates the project. If you model ten years you must also deduct service and network costs for years beyond the contract length.

## Revenue
6 · REVENUE ASSUMPTIONS
Every one of these will be challenged by the customer. Set them where you can defend them.
Pricing
Retail price to driver ($/kWh) | 0.65
Delivered energy cost — leave blank, now derived |  | Derived from the tariff block at the foot of this tab. Set the figures there.
Utility subscription — leave blank, now derived |  | Customer charge plus demand charge, annualised, from the tariff block at the foot of this tab. On a demand schedule this is the largest number on the page.
Card processing fee (% of gross) | 3%
Idle fee revenue included? | No | Keep this No unless it is contracted
Utilisation — steady state
Hours per day the site is chargeable |  | From 1_Project
Stall occupancy (share of stalls used per day) | 20%
Charging hours per occupied stall, as share of open hours | 25%
Nameplate de-rate factor | 0.98 | Cabinet output vs label
Average delivered power, share of port rating | 70% | CHARGING-CURVE TAPER
Ramp and growth
Year 1 share of steady state | 50% | Greenfield sites take time to fill
Year 2 share of steady state | 75%
Year 3 share of steady state | 100%
Annual growth after ramp | 6% | Justify as a level, not a rate
Historical actuals — replacement sites only, leave blank for greenfield
Months of history available
Historical kWh dispensed per day
Historical gross revenue per year
Historical net profit per year
Ports in service on an average day
Share of sessions under 1 kWh |  | Failed-session rate
Utility rate selection — drives the delivered energy cost
Pick the utility and schedule and the model derives $/kWh and the subscription from the tariff. No blended guess required.
Utility |  | Reads the utility named on the Project tab. Set it there.
Rate schedule | TOU-EV-9 | Pick the schedule this site will actually take. The list is on the Utilities tab under RATE SCHEDULE PICKER; add the schedule there first if it is not on it.
Service voltage level | Secondary | Secondary or primary. On schedules that price them differently this changes the rate.
Share of energy dispensed on-peak | 30% | Only if the schedule has time-of-use periods, and then from ITS periods — not from a remembered 4-9 pm peak. Leave all three blank on a flat schedule.
Share off-peak | 55%
Share super off-peak | 15% | The three shares must sum to 100% where they are used at all.
Expected peak concurrency (ports drawing at once) |  | DERIVED, not typed. Average concurrent ports is the day's energy over twenty-four hours of average delivered power; the peak-to-average factor above turns that into a peak. Rounded up, because you cannot subscribe to a fraction of a port.
Subscribed kW |  | Peak concurrent ports at the sizing basis above, plus the safety margin. This follows the Subscription policy row: set it to "Subscribe at full nameplate" and this becomes the whole connected load instead. A site is built for its peak and paid for its average, and on a schedule that sells capacity in blocks the difference between the two is the largest operating number in the project.
Market benchmarking
State for benchmarking | California | REQUIRED. Pick the market this projection should be tested against — the list is on RefData under MARKET BENCHMARKS. There is no default: this used to say California on every project regardless of where the site was.
Expected site factor (% of the state average port) |  | Leave blank and the model derives it from your utilisation inputs
Demand subscription — how it should ramp
Demand charges are set by simultaneous draw, not annual energy. A site that fills gradually should not carry a full-nameplate subscription from day one.
Subscription policy | Ramped to projected demand
Peak-to-average concurrency factor | 4 | Ratio of peak simultaneous draw to the daily average
Safety margin on subscribed kW | 20% | Headroom above projected peak before overage bites
Size demand on full port rating? | Yes | A vehicle at the start of a session draws full power
Interval data available from the utility? |  | Lets the subscription be trued up after two quarters
Annual tariff escalation | 0% | Applied to the demand and block rates year by year in the model. Zero holds the tariff flat for the whole horizon, which no utility has ever done — enter the utility's adopted or proposed path where there is one.
Revenue basis — greenfield benchmark or historical actuals
On a greenfield site the projection is built from market benchmarks, because there is nothing else. On a replacement site the projection should be built from the site's own history plus the uplifts stated on the Existing tab. Pick one. The model uses whichever is selected here.
Revenue basis | Historical actuals — replacement site | Switch to historical actuals on any site with twelve or more months of usable data.
Months of history available |  | From the Existing tab section E.
Historical kWh per year
Combined uplift multiple
Projected kWh per year — replacement basis |  | History times the stated uplifts. This is what the model uses when the basis above is set to historical actuals.
Which basis is in force? |  |  | A replacement site running on market benchmarks is throwing away its best evidence.
Historical price against the proposed price |  |  | A large price increase on a site with a settled driver base is a demand risk, not a revenue gain.
Historical delivered cost against the tariff estimate |  |  | Actual billing beats a tariff lookup every time. This is the number to carry into the model.
ON A REPLACEMENT SITE, THREE INPUTS ABOVE STOP BEING ASSUMPTIONS. Stall occupancy, the chargeable-hours share and the site factor are all greenfield estimating devices. Where twelve months of metered history exists they are superseded by it — leave them at default and let the historical basis drive the projection.
STEADY-STATE PROJECTION — the greenfield basis, computed here
The model used to compute this downstream, which meant nothing on this sheet could test it. It is computed here so the market cross-check on the Existing tab has something to read on a site with no history.
Power per position (kW)
Average delivered power (kW) |  | De-rated, then tapered
Charging stall-hours per day
Steady-state kWh per day
Steady-state kWh per year
Tariff provenance and rate-entry checks
Every revenue figure in the model rests on the rate figures above. This block records how much weight they can carry, and the proposal prints it at the point of use rather than in a risk register nobody reads.
Source of the rate figures | SCE TOU-EV rate fact sheet, July 2025 | Where each $/kWh and fixed charge came from — a filed tariff sheet, a rate insert, a bill, or a phone call. Name it. The proposal prints this.
Verified against the filed tariff sheets? | No | Yes / No. "No" is a perfectly good answer and the proposal will say so at the point of use; what is not acceptable is nobody knowing.
Verified by / date | VP · 2026-09-01 | Who checked it, and when.
Demand-schedule eligibility threshold |  | If this utility moves a customer onto a demand schedule above some monthly consumption, record the threshold and its units here. Leave blank if unknown — blank prints as unconfirmed, which is honest. A figure typed from memory is not.
Would this site cross that threshold? |  | Against the steady-state projection at the foot of this tab. If yes, the tariff behind every revenue figure in the model is the wrong one.
Time-of-use shares entered? |  | Blank on a flat schedule is the right answer. A split that does not sum to 100% is not.
Tariff figures — the bill, decomposed
One row per component of the bill, so a demand charge cannot hide inside a blended cents-per-kWh figure. Take them from the schedule row in the RateLibrary tab.
Volumetric energy cost ($/kWh) | 0.28 | The per-kWh charge on the chosen schedule, before fixed and demand charges.
Customer charge ($/month) | 701.42 | The fixed monthly meter charge.
Demand charge ($/kW-month) | 0 | Zero on a schedule with no demand charge. This is the figure that decides whether a fast charging site works: at low load factor a demand charge can cost more than all the energy.
Billing demand assumed (kW) |  | What the meter will see as the monthly maximum. Full nameplate unless load management caps it. Every kW here costs the demand charge above, twelve times a year.
Annual fixed and demand cost ($/yr) |  | Customer charge plus any demand charge, annualised, PLUS the subscription. The Revenue tab's utility subscription line reads this row and the project model reads that. Until 2.9.0 the subscription was not in it at all, so a schedule that sells capacity in blocks was costing nothing.
DEMAND SUBSCRIPTION — WHAT THE RAMP ABOVE COSTS
A schedule that sells capacity in blocks charges for what you subscribe to, not what you draw. The subscribed figure comes from the ramp above; the block size and price come from the rate library. If the library has no block for this schedule the cost is zero and the check at the foot of this block says so rather than letting the zero pass for an answer.
Subscription block size (kW) |  | From the rate library row for this utility and schedule. Zero means the library has no block size for it — not that the schedule has no blocks.
Subscription block price ($/block/month) |  | From the same library row.
Blocks subscribed |  | Subscribed kW over the block size, rounded up.
Subscription cost ($/yr) |  | Blocks times the block price times twelve. This is the line that decides whether a high-capacity, low-utilisation site works.
Subscription cost basis |  | If this reads UNPRICED, check the rate library row for the schedule named above BEFORE asking the utility for figures — a lookup pointing at the wrong cell returns zero exactly the same way a missing library row does.
Note on B7: PG&E business EV rates use a subscribed-kW block (about $95.56 per 50 kW) billed at double for overage. On a large DC site this is tens of thousands a year and it does not shrink when volume is low. Never leave it at zero without checking a bill.
Note on B16: Vehicles taper as the pack fills. Average delivered power across a DC session runs about 55-70% of the port rating. Setting this to 1.00 models every minute at full power, which no vehicle accepts, and overstates revenue by roughly 43%.
Note on B22: National per-port DCFC utilisation has been roughly flat for five quarters — new ports absorb demand growth. Defend a growth rate by showing where the site sits against sessions-per-port benchmarks, not by asserting a percentage.
Note on B36: PG&E splits at 100 kW: BEV-1 below, BEV-2 above. Secondary or primary voltage changes the block price. SCE splits at 20 kW and 500 kW. SDG&E EV-HP splits at 150 kW.
Note on B41: The subscription is a billing construct, not a physical limit. Subscribing to realistic peak concurrency instead of full nameplate is often the largest controllable saving on a big DC site — but overage is billed at roughly double, so leave headroom.
Note on B46: A new site should not be modelled at the state average. Stating the site factor openly is far more defensible than asserting a growth rate.
Note on B51: Ramping the subscription with projected concurrency is usually worth six figures across ten years. The trade is overage exposure at roughly double the base rate if concurrency runs ahead of forecast.
Note on B52: Public fast charging clusters into mornings, evenings and weekends, so the peak fifteen-minute demand runs several times the daily average. Three to six is the usual range.
Note on B54: The charging-curve taper reduces energy across a session. It does not reduce instantaneous draw. Demand is a fifteen-minute peak, so size on full port rating.

## Carbon
7 · CARBON CREDITS AND INCENTIVES
The FCI capacity credit is usually the most reliable revenue in the model. Treat its inputs accordingly.
LCFS / FCI capacity credit
Site qualifies for FCI capacity credits? | Yes | Yes / No / Pending
Permit clears the 1 Jan 2022 test? | Yes | Yes / No
Application filed? | No | Yes / No — with date
Registered aggregator | Registered aggregator LLC
Aggregator share of credit value | 5% | Third-party administrator. Not our scope — a deduction from proceeds, disclosed as a cost.
FCI credit rate ($/kW/yr) | 71.6667 | Confirm with the aggregator in writing
Crediting period (years) | 10
Gross capacity credit per year |  | DC fast-charging capacity only — the FCI credit does not pay on Level 2.
Net of aggregator share, per year
Gross across crediting period
Consumption credits (Level 2)
L2 consumption credit ($/kWh) | 0.0045
Site-total L2 kWh per day |  | SITE total, not per port
Cap test
Cap multiple of net capex | 1.5 | FCI revenue stops at this multiple
Grants or rebates awarded | 0 | Reduces net capex and therefore the cap
Federal and state incentives
Federal ITC claimed? | No | Sec 30C ended for property in service after 30 Jun 2026
State programme evaluated | Fast Charge California | e.g. Fast Charge California — name it even if it does not qualify
State programme outcome | Does not qualify | Qualifies / Does not qualify / Applied — with the reason
Note on B10: This rate embeds an assumed LCFS credit price. Ask the aggregator what price it assumes, whether the rate scales linearly to this cabinet size, and whether the credit is computed per cabinet or per connector.
Note on B22: A grant reduces net capital expenditure, which lowers the 1.5x cap and can truncate the capacity credit. On a large DC site a grant can cost more credit than it pays. Model both cases before recommending one.

## Deal_Structure
8 · DEAL STRUCTURE (OPTIONAL)
Leave every knob at zero for a straight sale. Fill them in only when we are trading price for a share of the upside.
• | This tab is optional. Zero everywhere means a conventional sale and the model runs exactly as it does today.
• | Use it when we want to lower the client's price in return for keeping part of the carbon credit or the charging revenue.
• | The model reports both sides — what the client nets and what we net on the capital we put in — so a structure can be judged before it is offered.
What we keep
Structure name | Carbon share test | A label so a reader knows which structure this is
Our share of the net carbon credit | 50% | 0% = client keeps all of it
Our share of charging revenue | 10% | 0% = client keeps all of it
Revenue share is taken on | Net charging profit | Net charging profit / Gross revenue
Share runs for (years) | 10 | Cannot exceed the model horizon
What we give in return
Extra discount on charger hardware | 5% | On top of the discount already in the base price
Extra discount on electrical and construction | 0%
Extra discount on service, warranty and network | 0%
Direct capital contribution | 100000 | Cash or hardware we fund outright
Guard rails — the model will report against these
Minimum acceptable client NPV | 0 | Below this the structure is not worth offering
Minimum acceptable return on our capital | 2 | Multiple of what we contribute
Maximum capital we will contribute | 150000 | Hard ceiling on our exposure
Price position |  | What we are doing about the guard rails above, and what would change it. A price held on judgement with no written release trigger is a price that quietly drifts — name the evidence or the event that would move it.
Scope of supply — which lines do we provide?
Default is all of them, which is the base case. Mark a line "By others" when a third party supplies it — it leaves our contract but stays in the client's project.
Service line | Who provides it | Third party name | Notes
Charger hardware — procurement and sale | We provide
Extended warranty and O&M service | We provide
EVOLV platform and commissioning | We provide
Sales tax on chargers | We provide
Design and engineering | By others
Construction — all-inclusive (materials, equipment, labour) | We provide
Utility interconnection management | We provide
Carbon credit administration is NOT one of our lines — a third-party aggregator takes a share of proceeds. See 7_Carbon.
Handing a line to a third party removes its price and its margin. The model shows what each one is worth before you offer it.
Financing basis
Client finances | Whole project | Whether the facility covers third-party scope too
Note on B10: Credit ownership has to be assigned contractually and the aggregator agreement must permit it. A revenue share is not the same thing as owning the credit — be clear which one is being sold.
Note on B12: A share of GROSS pays us before the site has covered its energy cost. A share of NET profit shares the downside as well as the upside. They are very different deals.

## Overrides
9 · OVERRIDE REGISTER
The escape hatch. Force any derived value here when you know better than the engine — a quote, a fee schedule, a field measurement.
• | Leave a row blank and the engine uses its own computed number. Fill it in and the engine uses yours, everywhere.
• | Every override is reported on the model summary, so a reviewer can always see that the model was touched and exactly where.
• | Put the reason in the last column. An override with no reason is indistinguishable from a typo six months later.
Value | Override | Units | Why — quote, fee schedule, measurement
Wires, conduits and peripherals (before uplift) |  | $
Switchgear and distribution (before uplift) | 150000 | $ | Vendor quote for the switchboard
Site works (before uplift) |  | $
Dump, waste and freight (before uplift) |  | $
Permits and plan check (before uplift) |  | $
Utility application and contract fees (before uplift) |  | $
Construction equipment rentals (before uplift) |  | $
Design and engineering |  | $
Utility line-extension contribution (if any) |  | $ | Leave blank and it is excluded by name in the proposal. Fill it in only when PG&E returns a design that requires it.
Additional or unforeseen scope |  | $
Standard frame (A) | 3200 | amps | Engineer's single line
Branch breaker per cabinet (A) |  | amps
Crew days on site |  | days
Steady-state kWh per day | 1400 | kWh | Traffic study, Aug 2026
Gross capacity credit per year |  | $
Monthly loan payment |  | $
Hardware MSRP each |  | $
Retail price to driver | 0.62 | $/kWh | Pricing committee
Delivered energy cost |  | $/kWh
Utility demand / subscription |  | $/yr

## PriceBook
Category | [7 empty] | CONNECTORS | HOW THE COUNT WAS DECIDED | SKU INDEX — built from the categories above; the capacity dropdown on 2_Equipment resolves against these columns
_L2 | CTX-R40-240-1 | 40A Single Home Charger | 605 |  |  |  |  | 1 | description says Single | Level 2 AC | 30 kW DC | 60 kW DC | 120 kW DC | 160 kW DC | 180 kW DC | 240 kW DC | 360 kW DC | V2G | Distributed system | Accessory | CAPACITY | RATED kW | PER PORT | ROLE BY SKU | ROLE | DISPENSERS
_L2 | CTX-R48-240-1 | 48A Single Home Charger | 605 |  |  |  |  | 1 | description says Single | CTX-R40-240-1 | TP5-30-480-1 | TP5-60-480-1 | TP5-120-480-1 | TP5-160-480-1 | TP5-180-480-1 | TP5-240-480-2-300 | TP5-360-480-1-300 | CTX-V2G-20-480-1 | CTX-DSPB-360 | CTX-FLUXPED | Level 2 AC | 7.2 | 1 | CTX-R40-240-1 | level_2 | CTX-DST-2-300
_L2 | CTX-C32-240-1 | 32A Single Commercial L2 Charger | 1402.5 |  |  |  |  | 1 | description says Single | CTX-R48-240-1 | TP5-30-480-3 | TP5-60-480-2 | TP5-120-480-2 | TP5-160-480-2 | TP5-180-480-2 | TP5-240-480-2-400 | TP5-360-480-2-300 | CTX-V2G-30-480-1 | CTX-DSPB-480 | CTX-FLUXWAL-CMS-1 | 30 kW DC | 30 | 0 | CTX-R48-240-1 | level_2 | CTX-DST-HPC-2-500/300
_L2 | CTX-C48-240-1 | 48A Single Commercial L2 Charger (18' Cable with Modem) | 1402.5 |  |  |  |  | 1 | description says Single | CTX-C32-240-1 |  | TP5-60-480-3 | TP5-120-480-2-300 | TP5-160-480-3 | TP5-180-480-2-300 | HPC-240-480-1 | TP5-360-480-3-300 | CTX-V2G-40-480-1 | CTX-DSPB-1280 | CTX-FLUXPED-CMS-1 | 60 kW DC | 60 | 0 | CTX-C32-240-1 | level_2
_L2 | CTX-C80-240-1 | 80A Single Commercial L2 Charger (18' Cable with Modem) | 1650 |  |  |  |  | 1 | description says Single | CTX-C48-240-1 |  | TP5-60-480-4 | TP5-120-480-3-300 | TP5-160-480-2-300 | TP5-180-480-3-300 | HPC-240-480-2 | TP5-360-480-4-300 | CTX-V2G-60-480-1 | CTX-DST-2-300 | CTX-FLUXPED-CMS-2 | 120 kW DC | 120 | 0 | CTX-C48-240-1 | level_2
_L2 | CTX-C40-240-2 | 40A Dual Commercial L2 Charger (18' Cable with Modem) | 1952.5 |  |  |  |  | 2 | description says Dual | CTX-C80-240-1 |  | CTX-AiO-60-2-200 | CTX-AiO-120-2-350 | HPC-160-480-1 | TP5-180-480-2-300-CL20 | CTX-AiO-240-2-300 | HPC-360-480-1 |  | CTX-DST-HPC-2-500/300 | CTX-FLUXPED-SBS | 160 kW DC | 160 | 0 | CTX-C80-240-1 | level_2
_L2 | CTX-C80-240-2 | 80A Dual Commercial L2 Charger (18' Cable with Modem) | 2194.5 |  |  |  |  | 2 | description says Dual | CTX-C40-240-2 |  | CTX-AiO-60-3-200 | CTX-AiO-120-3-350 | HPC-160-480-2 | TP5-180-480-2-BAA | CTX-AiO-240-3-300 | HPC-360-480-2 |  |  |  | 180 kW DC | 180 | 0 | CTX-C40-240-2 | level_2
_L2 | CTX-C80-240-1-ISO | 80A Single Commercial L2 Charger (18' Cable with Modem) | 2255 |  |  |  |  | 1 | description says Single | CTX-C80-240-2 |  | CTX-AiO-60-4-200 | CTX-AiO-120-4-350 | CTX-AiO-160-2-350 | TP5-180-480-3-BAA | CTX-AiO-240-4-300 | HPC-360-480-3 |  |  |  | 240 kW DC | 240 | 0 | CTX-C80-240-2 | level_2
_L2 | CTX-C40-240-2-ISO | 40A Dual Commercial L2 Charger (18' Cable with Modem) | 2530 |  |  |  |  | 2 | description says Dual | CTX-C80-240-1-ISO |  | TP5-60-480-2-BAA | CTX-AiO-120-5-350 | CTX-AiO-160-3-350 | TP5-180-480-4-BAA | CTX-AiO-240-5-300 | HPC-360-480-4 |  |  |  | 360 kW DC | 360 | 0 | CTX-C80-240-1-ISO | level_2
_L2 | CTX-C80-240-2-ISO | 80A Dual Commercial L2 Charger (18' Cable with Modem) | 2805 |  |  |  |  | 2 | description says Dual | CTX-C40-240-2-ISO |  | TP5-60-480-3-BAA | CTX-AiO-120-6-350 | CTX-AiO-160-4-350 | HPC-180-480-2-BAA |  | TP5-360-480-2-BAA |  |  |  | V2G | 0 | 0 | CTX-C40-240-2-ISO | level_2
_kW30 | TP5-30-480-1 | Gen2 30kW DCFC Wall Mount - 100 Amps / 1000VDC with CCS1 (~16ft) | 13750 | 30 |  |  |  | 1 | connectors named in the description | CTX-C80-240-2-ISO |  | TP5-60-480-4-BAA | TP5-120-480-2-300-BAA | CTX-AiO-160-5-350 | HPC-180-480-3-BAA |  | TP5-360-480-3-BAA |  |  |  | Distributed system | 0 | 0 | CTX-C80-240-2-ISO | level_2
_kW30 | TP5-30-480-3 | Gen 2Gen 30kW DCFC Wall Mount - 200 Amps / 1000VDC with NACS (~16ft) | 13750 | 30 |  |  |  | 1 | connectors named in the description |  |  |  | TP5-120-480-3-300-BAA | CTX-AiO-160-6-350 | HPC-180-480-4-BAA |  | TP5-360-480-4-BAA |  |  |  | Accessory | 0 | 0 | TP5-30-480-1 | all_in_one
_kW60 | TP5-60-480-1 | 60kW DCFC - 200 Amps / 1000VDC with CCS1 & NACS(~16ft) ; 4G Modem | 28500 | 60 |  |  |  | 2 | connectors named in the description |  |  |  | TP5-120-480-4-300-BAA |  |  |  | HPC-360-480-2-BAA | [6 empty] | TP5-30-480-3 | all_in_one
_kW60 | TP5-60-480-2 | 60kW DCFC - 200 Amps / 1000VDC with CCS1 & CCS1(~16ft) ; 4G Modem | 28500 | 60 |  |  |  | 2 | connectors named in the description | [7 empty] | HPC-360-480-3-BAA | [6 empty] | TP5-60-480-1 | all_in_one
_kW60 | TP5-60-480-3 | 60kW DCFC - 200 Amps / 1000VDC with CCS1 & NACS(~16ft) ; 4G Modem | 28500 | 60 |  |  |  | 2 | connectors named in the description | [7 empty] | HPC-360-480-4-BAA | [6 empty] | TP5-60-480-2 | all_in_one
_kW60 | TP5-60-480-4 | 60kW DCFC - 200 Amps / 1000VDC with NACS & NACS(~16ft) ; 4G Modem | 28500 | 60 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-60-480-3 | all_in_one
_kW60 | CTX-AiO-60-2-200 | Gen 2 60kW DCFC - 200 Amps / 1000VDC with CCS1 & CCS1(~16ft) ; 4G Modem | 31350 | 60 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-60-480-4 | all_in_one
_kW60 | CTX-AiO-60-3-200 | Gen 2 60kW DCFC - 200 Amps / 1000VDC with CCS1 & NACS(~16ft) ; 4G Modem | 31350 | 60 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-60-2-200 | all_in_one
_kW60 | CTX-AiO-60-4-200 | Gen 2 60kW DCFC - 200 Amps / 1000VDC with NACS & NACS(~16ft) ; 4G Modem | 31350 | 60 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-60-3-200 | all_in_one
_kW120 | TP5-120-480-1 | 120kW DCFC All In One Charger - 200 Amps / 1000VDC with CCS1 & NACS(~16ft) ; Can charge 2 cars simultaneously with 60kW each ; 4G Modem | 54000 | 120 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-60-4-200 | all_in_one
_kW120 | TP5-120-480-2 | 120kW DCFC All In One Charger - 200 Amps / 1000VDC with CCS1 & CCS1(~16ft); Can charge 2 cars simultaneously with 60kW each ; 4G Modem | 54000 | 120 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-120-480-1 | all_in_one
_kW120 | TP5-120-480-2-300 | 120kW DCFC All In One Charger - 350A Cable / 1000VDC with CCS1 & CCS1(~16ft); Can charge 2 cars simultaneously with 60kW each ; 4G Modem | 54000 | 120 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-120-480-2 | all_in_one
_kW120 | TP5-120-480-3-300 | 120kW DCFC All In One Charger - 1000VDC, Cables: 350A CCS1 & 400A NACS (~16ft); Can charge 2 cars simultaneously with 60kW each ; 4G Modem | 54000 | 120 |  |  |  | 2 | manual — description does not state the count | [14 empty] | TP5-120-480-2-300 | all_in_one
_kW120 | CTX-AiO-120-2-350 | Gen3 120kW CCS1 350A + CCS1 350A ; Cable Management + CC | 59400 | 120 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-120-480-3-300 | all_in_one
_kW120 | CTX-AiO-120-3-350 | Gen3 120kW CCS1 350A + NACS 350A ; Cable Management + CC | 59400 | 120 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-120-2-350 | all_in_one
_kW120 | CTX-AiO-120-4-350 | Gen3 120kW NACS 350A + NACS 350A ; Cable Management + CC | 59400 | 120 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-120-3-350 | all_in_one
_kW120 | CTX-AiO-120-5-350 | Gen3 120kW Single CCS1 350A ; Cable Management + CC | 59400 | 120 |  |  |  | 1 | description says Single | [14 empty] | CTX-AiO-120-4-350 | all_in_one
_kW120 | CTX-AiO-120-6-350 | Gen3 120kW Single NACS 350A ; Cable Management + CC | 59400 | 120 |  |  |  | 1 | description says Single | [14 empty] | CTX-AiO-120-5-350 | all_in_one
_kW160 | TP5-160-480-1 | 160kW DCFC All In One Charger - 200 Amps / 1000VDC with CCS1 & NACS(~16ft); It can dispense 200A on single connector and can charge 2 cars simultaneously with 80kW eac | 57000 | 160 |  |  |  | 1 | description says Single | [14 empty] | CTX-AiO-120-6-350 | all_in_one
_kW160 | TP5-160-480-2 | 160kW DCFC All In One Charger - 200 Amps / 1000VDC with CCS1 & CCS1(~16ft); It can dispense 200A on single connector and can charge 2 cars simultaneously with 80kW each ; | 57000 | 160 |  |  |  | 1 | description says Single | [14 empty] | TP5-160-480-1 | all_in_one
_kW160 | TP5-160-480-3 | 160kW DCFC All In One Charger - 200 Amps / 1000VDC with CCS1 & NACS (~16ft); It can dispense 200A on single connector and can charge 2 cars simultaneously with 80kW each | 57000 | 160 |  |  |  | 1 | description says Single | [14 empty] | TP5-160-480-2 | all_in_one
_kW160 | TP5-160-480-2-300 | 160kW DCFC All In One Charger - 350A Cable / 1000VDC with CCS1 & CCS1(~16ft); Can charge 2 cars simultaneously with 80kW each ; 4G Modem | 57000 | 160 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-160-480-3 | all_in_one
_kW160 | HPC-160-480-1 | 160kW HPC All In One Charger - 400 Amps / 1000VDC with Liquid Cooled Connector for CCS1(~14ft) & NACS(~16ft) ; It can deliver 400A on the CCS coonnector. Can charge 2 | 68000 | 160 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-160-480-2-300 | all_in_one
_kW160 | HPC-160-480-2 | 160kW HPC All In One Charger - 400 Amps / 1000VDC with Liquid Cooled Connector for CCS1(~14ft) & NACS(~16ft) ; It can deliver 400A on the CCS coonnector. Also can char | 70000 | 160 |  |  |  | 2 | connectors named in the description | [14 empty] | HPC-160-480-1 | all_in_one
_kW160 | CTX-AiO-160-2-350 | Gen3 160kW CCS1 350A + CCS1 350A ; Cable Management + CC | 68200 | 160 |  |  |  | 2 | connectors named in the description | [14 empty] | HPC-160-480-2 | all_in_one
_kW160 | CTX-AiO-160-3-350 | Gen3 160kW CCS1 350A + NACS 350A ; Cable Management + CC | 68200 | 160 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-160-2-350 | all_in_one
_kW160 | CTX-AiO-160-4-350 | Gen3 160kW NACS 350A + NACS 350A ; Cable Management + CC | 68200 | 160 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-160-3-350 | all_in_one
_kW160 | CTX-AiO-160-5-350 | Gen3 160kW Single CCS1 350A ; Cable Management + CC | 68200 | 160 |  |  |  | 1 | description says Single | [14 empty] | CTX-AiO-160-4-350 | all_in_one
_kW160 | CTX-AiO-160-6-350 | Gen3 160kW Single NACS 350A ; Cable Management + CC | 68200 | 160 |  |  |  | 1 | description says Single | [14 empty] | CTX-AiO-160-5-350 | all_in_one
_kW180 | TP5-180-480-1 | 180kW DCFC All In One Charger - 200 Amps / 1000VDC with CCS1 & NACS(~16ft); Can charge 2 cars simultaneously with 90kW each or 120kW on CCS1 and 60kW on NACS; 4G Mo | 62000 | 180 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-160-6-350 | all_in_one
_kW180 | TP5-180-480-2 | 180kW DCFC All In One Charger - 200 Amps / 1000VDC with CCS1 & CCS1(~16ft); Can charge 2 cars simultaneously with 90kW each ; 4G Modem | 62000 | 180 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-180-480-1 | all_in_one
_kW180 | TP5-180-480-2-300 | 180kW DCFC All In One Charger - 350A Cable / 1000VDC with CCS1 & CCS1(~16ft); Can charge 2 cars simultaneously with 90kW each ; 4G Modem | 62000 | 180 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-180-480-2 | all_in_one
_kW180 | TP5-180-480-3-300 | 180kW DCFC All In One Charger - 1000VDC, Cables: 350A CCS1 & 400A NACS (~16ft); Can charge 2 cars simultaneously with 90kW each ; 4G Modem | 62000 | 180 |  |  |  | 2 | manual — description does not state the count | [14 empty] | TP5-180-480-2-300 | all_in_one
_kW180 | TP5-180-480-2-300-CL20 | 180kW DCFC All In One Charger - 350A Cable / 1000VDC with CCS1 & CCS1(~20ft); Can charge 2 cars simultaneously with 90kW each ; 4G Modem | 62000 | 180 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-180-480-3-300 | all_in_one
_kW240 | TP5-240-480-2-300 | 240kW DCFC All In One Charger - 350A Cable / 1000VDC Dual CCS1 ; Can charge 2 cars simultaneously with 120kW each ; 4G Modem | 80000 | 240 |  |  |  | 2 | description says Dual | [14 empty] | TP5-180-480-2-300-CL20 | all_in_one
_kW240 | TP5-240-480-2-400 | 240kW DCFC All In One Charger - 1000VDC, Cables: 350A CCS1 & 400A NACS; Can charge 2 cars simultaneously with 120kW each ; 4G Modem | 80000 | 240 |  |  |  | 2 | manual — description does not state the count | [14 empty] | TP5-240-480-2-300 | all_in_one
_kW240 | HPC-240-480-1 | 240kW HPC All In One Charger - 500 Amps / 1000VDC with Liquid Cooled Connector for CCS1 & NACS(~14ft) ; Can deliver 500A on CCS coonnector. Can charge 2 cars simultane | 98000 | 240 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-240-480-2-400 | all_in_one
_kW240 | HPC-240-480-2 | 240kW HPC All In One Charger - 500 Amps / 1000VDC with Liquid Cooled Connector for Dual CCS1 ; Can deliver 450A on one CCS coonnector and 250A on each connector if used s | 98000 | 240 |  |  |  | 2 | description says Dual | [14 empty] | HPC-240-480-1 | all_in_one
_kW240 | CTX-AiO-240-2-300 | Gen3 240kW CCS1 350A + CCS1 350A; Cable Management + CC | 88000 | 240 |  |  |  | 2 | connectors named in the description | [14 empty] | HPC-240-480-2 | all_in_one
_kW240 | CTX-AiO-240-3-300 | Gen3 240kW CCS1 350A + NACS 350A; Cable Management + CC | 88000 | 240 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-240-2-300 | all_in_one
_kW240 | CTX-AiO-240-4-300 | Gen3 240kW NACS 350A + NACS 350A; Cable Management + CC | 88000 | 240 |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-AiO-240-3-300 | all_in_one
_kW240 | CTX-AiO-240-5-300 | Gen3 240kW Single CCS1 350A; Cable Management + CC | 88000 | 240 |  |  |  | 1 | description says Single | [14 empty] | CTX-AiO-240-4-300 | all_in_one
_kW360 | TP5-360-480-1-300 | 360kW DCFC All In One Charger - 1000VDC, Cables: 350A CCS1 & NACS ; Can charge 2 cars simultaneously with 180kW each ; 4G Modem | 99000 | 360 |  |  |  | 2 | manual — description does not state the count | [14 empty] | CTX-AiO-240-5-300 | all_in_one
_kW360 | TP5-360-480-2-300 | 360kW DCFC All In One Charger - 350A Cable / 1000VDC Dual CCS1 ; Can charge 2 cars simultaneously with 180kW each ; 4G Modem | 99000 | 360 |  |  |  | 2 | description says Dual | [14 empty] | TP5-360-480-1-300 | all_in_one
_kW360 | TP5-360-480-3-300 | 360kW DCFC All In One Charger - 1000VDC, Cables: 350A CCS1 & 400A NACS ; Can charge 2 cars simultaneously with 180kW each ; 4G Modem | 99000 | 360 |  |  |  | 2 | manual — description does not state the count | [14 empty] | TP5-360-480-2-300 | all_in_one
_kW360 | TP5-360-480-4-300 | 360kW DCFC All In One Charger - 1000VDC, Cables: 400A NACS / 400A NACS ; Can charge 2 cars simultaneously with 180kW each ; 4G Modem | 99000 | 360 |  |  |  | 2 | manual — description does not state the count | [14 empty] | TP5-360-480-3-300 | all_in_one
_kW360 | HPC-360-480-1 | 360kW HPC All In One Charger - 500 Amps / 1000VDC with Liquid Cooled Connector for CCS1 & NACS(~14ft) ; Can deliver 500A on CCS coonnector. Can charge 2 cars simultane | 110000 | 360 |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-360-480-4-300 | all_in_one
_kW360 | HPC-360-480-2 | 360kW HPC All In One Charger - 500 Amps / 1000VDC with Liquid Cooled Connector for Dual CCS1 ; Can deliver 500A on one CCS coonnector and 400A on each connector if used s | 110000 | 360 |  |  |  | 2 | description says Dual | [14 empty] | HPC-360-480-1 | all_in_one
_kW360 | HPC-360-480-3 | 360kW HPC All In One Charger - 500 Amps / 1000VDC with Liquid Cooled Connector for CCS1 & NACS ; Can deliver 500A on CCS coonnector. Can charge 2 cars simultaneously; 4G | 110000 | 360 |  |  |  | 2 | connectors named in the description | [14 empty] | HPC-360-480-2 | all_in_one
_kW360 | HPC-360-480-4 | 360kW HPC All In One Charger - 500 Amps / 1000VDC with Liquid Cooled Connector for NACS / NACS ; Can deliver 500A on CCS coonnector. Can charge 2 cars simultaneously; 4G | 110000 | 360 |  |  |  | 2 | connectors named in the description | [14 empty] | HPC-360-480-3 | all_in_one
_Distributed_System | CTX-DSPB-360 | 360kW Tower | 81400 | 360 |  |  |  |  | distributed system — the architecture table holds this | [14 empty] | HPC-360-480-4 | all_in_one
_Distributed_System | CTX-DSPB-480 | 480kW Tower | 90200 | 480 |  |  |  |  | distributed system — the architecture table holds this | [14 empty] | CTX-DSPB-360 | power_cabinet
_Distributed_System | CTX-DSPB-1280 | 1,280kW Tower | 225000 | 1280 |  |  |  |  | distributed system — the architecture table holds this | [14 empty] | CTX-DSPB-480 | power_cabinet
_Distributed_System | CTX-DST-2-300 | Dispenser 300/300 | 35200 | [5 empty] | distributed system — the architecture table holds this | [14 empty] | CTX-DSPB-1280 | power_cabinet
_Distributed_System | CTX-DST-HPC-2-500/300 | Dispenser 500/300 | 49500 | [5 empty] | distributed system — the architecture table holds this | [14 empty] | CTX-DST-2-300 | dispenser
_Buy_America | TP5-60-480-2-BAA | Buy America NEVI Compliant, Assembled in CA, USA 60kW DCFC - 140 Amps / 1000VDC with CCS1 & CCS1(~16ft) ; 4G Modem | 68200 |  |  |  |  | 2 | connectors named in the description | [14 empty] | CTX-DST-HPC-2-500/300 | dispenser
_Buy_America | TP5-60-480-3-BAA | Buy America NEVI Compliant, Assembled in CA, USA 60kW DCFC - 140 Amps / 1000VDC with CCS1 & NACS ; 4G Modem | 68200 |  |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-60-480-2-BAA | all_in_one
_Buy_America | TP5-60-480-4-BAA | Buy America NEVI Compliant, Assembled in CA, USA 60kW DCFC - 140 Amps / 1000VDC with NACS & NACS ; 4G Modem | 68200 |  |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-60-480-3-BAA | all_in_one
_Buy_America | TP5-120-480-2-300-BAA | Buy America NEVI Compliant, Assembled in CA, USA 120kW DCFC All In One Charger - 350A Cable / 1000VDC with CCS1 & CCS1(~16ft); Can charge 2 cars simultaneously with 60kW | 75900 |  |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-60-480-4-BAA | all_in_one
_Buy_America | TP5-120-480-3-300-BAA | Buy America NEVI Compliant, Assembled in CA, USA 120kW DCFC All In One Charger - 350A Cable / 1000VDC with CCS1 & NACS; Can charge 2 cars simultaneously with 60kW each ; | 75900 |  |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-120-480-2-300-BAA | all_in_one
_Buy_America | TP5-120-480-4-300-BAA | Buy America NEVI Compliant, Assembled in CA, USA 120kW DCFC All In One Charger - 350A Cable / 1000VDC with NACS & NACS(~16ft); Can charge 2 cars simultaneously with 60kW | 75900 |  |  |  |  | 2 | connectors named in the description | [14 empty] | TP5-120-480-3-300-BAA | all_in_one
_Buy_America | TP5-180-480-2-BAA | Buy America NEVI Compliant, Assembled in CA, USA 180kW Air Cooled 350A Cable (BAA) CCS1 / CCS1 1000VDC Connector for Dual CCS1; Can deliver 350A on one CCS conector. Set | 82500 |  |  |  |  | 2 | description says Dual | [14 empty] | TP5-120-480-4-300-BAA | all_in_one
_Buy_America | TP5-180-480-3-BAA | Buy America NEVI Compliant, Assembled in CA, USA 180kW Air Cooled 350A Cable (BAA) CCS1 / NACS 1000VDC Connector for Dual CCS1; Can deliver 350A on one CCS conector. Set | 82500 |  |  |  |  | 2 | description says Dual | [14 empty] | TP5-180-480-2-BAA | all_in_one
_Buy_America | TP5-180-480-4-BAA | Buy America NEVI Compliant, Assembled in CA, USA 180kW Air Cooled 350A Cable (BAA) NACS / NACS 1000VDC Connector for Dual CCS1; Can deliver 350A on one CCS conector. Set | 82500 |  |  |  |  | 2 | description says Dual | [14 empty] | TP5-180-480-3-BAA | all_in_one
_Buy_America | HPC-180-480-2-BAA | Buy America NEVI Compliant, Assembled in CA, USA 180kW Liquid Cooled (BAA) Dual CCS1 500 Amps / 1000VDC with Liquid Cooled Connector for Dual CCS1 ; Can deliver 450A on o | 82500 |  |  |  |  | 2 | description says Dual | [14 empty] | TP5-180-480-4-BAA | all_in_one
_Buy_America | HPC-180-480-3-BAA | Buy America NEVI Compliant, Assembled in CA, USA 180kW Liquid Cooled (BAA) CCS1 / NACS 1000VDC with Liquid Cooled Connector for Dual CCS1 ; Can deliver 450A on one CCS co | 82500 |  |  |  |  | 2 | description says Dual | [14 empty] | HPC-180-480-2-BAA | all_in_one
_Buy_America | HPC-180-480-4-BAA | Buy America NEVI Compliant, Assembled in CA, USA 180kW Liquid Cooled (BAA) NACS /NACS 1000VDC with Liquid Cooled Connector for Dual CCS1 ; Can deliver 450A on one CCS con | 82500 |  |  |  |  | 2 | description says Dual | [14 empty] | HPC-180-480-3-BAA | all_in_one
_Buy_America | TP5-360-480-2-BAA | Buy America NEVI Compliant 360kW Air Cooled 350A Cable (BAA) Dual CCS1 / 1000VDC Connector for Dual CCS1 ; Can deliver 350A on one CCS connector and 350A on each connecto | 138600 |  |  |  |  | 2 | description says Dual | [14 empty] | HPC-180-480-4-BAA | all_in_one
_Buy_America | TP5-360-480-3-BAA | Buy America NEVI Compliant 360kW Air Cooled 350A Cable (BAA) Dual CCS1 / 1000VDC Connector for CCS1/NACS ; Can deliver 350A on one CCS connector and 350A on each connecto | 138600 |  |  |  |  | 2 | description says Dual | [14 empty] | TP5-360-480-2-BAA | all_in_one
_Buy_America | TP5-360-480-4-BAA | Buy America NEVI Compliant 360kW Air Cooled 350A Cable (BAA) Dual CCS1 / 1000VDC Connector for NACS/NACS ; Can deliver 350A on one CCS connector and 350A on each connecto | 138600 |  |  |  |  | 2 | description says Dual | [14 empty] | TP5-360-480-3-BAA | all_in_one
_Buy_America | HPC-360-480-2-BAA | Buy America NEVI Compliant 360kW Liquid Cooled (BAA) 500 Amps / 1000VDC with Liquid Cooled Connector for Dual CCS1 ; Can deliver 500A on one CCS connector and 400A on eac | 137500 |  |  |  |  | 2 | description says Dual | [14 empty] | TP5-360-480-4-BAA | all_in_one
_Buy_America | HPC-360-480-3-BAA | Buy America NEVI Compliant 360kW Liquid Cooled (BAA) 500 Amps / 1000VDC with Liquid Cooled Connector for CCS1/NACS ; Can deliver 500A on one CCS connector and 400A on eac | 137500 |  |  |  |  | 2 | connectors named in the description | [14 empty] | HPC-360-480-2-BAA | all_in_one
_Buy_America | HPC-360-480-4-BAA | Buy America NEVI Compliant 360kW Liquid Cooled (BAA) 500 Amps / 1000VDC with Liquid Cooled Connector for NACS/NACS ; Can deliver 500A on one CCS connector and 400A on eac | 137500 |  |  |  |  | 2 | connectors named in the description | [14 empty] | HPC-360-480-3-BAA | all_in_one
_V2G | CTX-V2G-20-480-1 | 20kW V2G Charger | 16700 |  |  |  |  | 1 | manual — description does not state the count | [14 empty] | HPC-360-480-4-BAA | all_in_one
_V2G | CTX-V2G-30-480-1 | 30kW V2G Charger | 23800 |  |  |  |  | 1 | manual — description does not state the count | [14 empty] | CTX-V2G-20-480-1 | all_in_one
_V2G | CTX-V2G-40-480-1 | 40kW V2G Charger | 35900 |  |  |  |  | 1 | manual — description does not state the count | [14 empty] | CTX-V2G-30-480-1 | all_in_one
_V2G | CTX-V2G-60-480-1 | 60kW V2G Charger | 50000 |  |  |  |  | 1 | manual — description does not state the count | [14 empty] | CTX-V2G-40-480-1 | all_in_one
_L2_Accessories | CTX-FLUXPED | Single Post (no Retraction) | 412.5 |  |  |  |  | 0 | accessory — not a charging position | [14 empty] | CTX-V2G-60-480-1 | all_in_one
_L2_Accessories | CTX-FLUXWAL-CMS-1 | Single Retractor (Wall) | 275 |  |  |  |  | 0 | accessory — not a charging position | [14 empty] | CTX-FLUXPED | accessory
_L2_Accessories | CTX-FLUXPED-CMS-1 | Single Retractor post | 412.5 |  |  |  |  | 0 | accessory — not a charging position | [14 empty] | CTX-FLUXWAL-CMS-1 | accessory
_L2_Accessories | CTX-FLUXPED-CMS-2 | Dual Retractor (Post) | 632.5 |  |  |  |  | 0 | accessory — not a charging position | [14 empty] | CTX-FLUXPED-CMS-1 | accessory
_L2_Accessories | CTX-FLUXPED-SBS | Side By Side Bracket | 137.5 |  |  |  |  | 0 | accessory — not a charging position | [14 empty] | CTX-FLUXPED-CMS-2 | accessory
[24 empty] | CTX-FLUXPED-SBS | accessory
SERVICE AND WARRANTY RATES PER CABINET PER YEAR
Class |  | Yearly warranty | In-warranty service | Warranty + service, year 3+ | Out-of-warranty service | Included manufacturer warranty
AC Charger - 7.2 kW UP80J-PMP Single |  | 416 | 320.11 | 736.11 | NOT OFFERED | 1 year, parts only
AC Charger - 2 x 7.2 kW UP160J-PMP Dual |  | 416 | 320.11 | 736.11 | NOT OFFERED | 1 year, parts only
AC Charger - 7.2 kW UP80J-WMP Single |  | 416 | 320.11 | 736.11 | NOT OFFERED | 1 year, parts only
AC Charger - 2 x 7.2 kW UP160J-WMP Dual |  | 416 | 320.11 | 736.11 | NOT OFFERED | 1 year, parts only
DC-60kW CCS1 + NACS |  | 962.84 | 1476.36 | 2439.2 | NOT OFFERED | 2 years, parts only
DC-120kW CCS1 + NACS |  | 1196.91 | 1616.76 | 2813.67 | NOT OFFERED | 2 years, parts only
DC-160kW CCS1 + NACS |  | 1428.57 | 1879.2 | 3307.77 | NOT OFFERED | 2 years, parts only
DC-180KW |  | 1856.844 | 2708.64 | 4565.484 | NOT OFFERED | 2 years, parts only
DC-240KW |  | 2708.64 | 6478.754 | 9187.394 | NOT OFFERED | 2 years, parts only
DC-360kW CCS1 + CCS1 |  | 4051.08 | 4898.88 | 8949.96 | NOT OFFERED | 2 years, parts only
CTX-DSPB-360 |  |  |  |  | NOT OFFERED | 2 years, parts only
CTX-DSPB-480 |  |  |  |  | NOT OFFERED | 2 years, parts only
CTX-DSPB-1280 |  |  |  |  | NOT OFFERED | 2 years, parts only
CTX-DST-2-300/CTX-DST-HPC-2-500/300 |  | 962.84 | 1476.36
Service is sold only against a warranty in force — the included manufacturer term or a paid extension of it. Zero Impact Energy does not normally service equipment carrying no warranty, which is why the rate is called in-warranty service. The out-of-warranty column is deliberately "NOT OFFERED" rather than blank: a blank reads as zero to anything that consumes this table.
The year-3+ rate is the yearly warranty plus the in-warranty service rate. Extending the warranty does not change what service costs; it adds back the warranty the manufacturer previously gave.
EQUIPMENT ARCHITECTURE — what each SKU is, not just what it costs
A power cabinet takes AC and produces DC and has no connectors. A dispenser has the connectors and no power of its own. An all-in-one is both in one enclosure. The role decides whether a row adds load, ports, both or neither — see 2_Equipment.
SKU | Role | DC output kW | AC input kW | AC input circuits | AC FLA total | DC outputs / connectors | Max dual dispensers | Source and confidence
CTX-DSPB-360 | Power cabinet — no connectors | 360 | 393 | 2 | 472.7 | 6 | 3 | DERIVED — AC input, circuit count and the 3-dispenser limit extrapolated from the published 480 kW cabinet. Confirm all three with Chargetronix before sizing service.
CTX-DSPB-480 | Power cabinet — no connectors | 480 | 524 | 2 | 630.3 | 6 | 3 | PUBLISHED — 480 VAC +/-10%, 3P+PE, 2 input circuits at 315 A each, input power 524 kW, output 480 kW, 200-1000 VDC, 500 A per channel, 1,600 A system, up to 6 DC outputs, dynamic power sharing in 40 kW increments. Takes UP TO 3 DUAL DISPENSERS (6 connectors).
CTX-DSPB-1280 | Power cabinet — no connectors | 1280 | 1397.3 | 6 | 1680.7 | 16 | 8 | PART PUBLISHED — 1,280 kW output, 480 VAC, 200-1000 VDC, 500 A per output, 4,267 A total, 16 connectors max — so UP TO 8 DUAL DISPENSERS. AC input power and circuit count are DERIVED; confirm with Chargetronix before sizing service.
CTX-DST-2-300 | Dispenser — connectors only | 0 | 0 | 0 | 0 | 2 | 0 | PUBLISHED — 2 connectors CCS1/NACS, 200-1000 V, up to 2 input circuits per dispenser, load sharing across 2 EVs, 5 m cable, 15 in touchscreen, 241 kg.
CTX-DST-HPC-2-500/300 | Dispenser — connectors only | 0 | 0 | 0 | 0 | 2 | 0 | PUBLISHED — liquid-cooled connector rated 500 A, air-cooled 200/350 A boost to 400 A.
MISSING FROM THE PRICE BOOK — Nexus Fleet Dispenser |  | single connector, CCS1/NACS air cooled 200/350 A, 50 kg, 5 m or 7 m cable, no user interface — in the published range but absent from the price book, so it cannot be quoted.

## RefData
REFERENCE DATA
Lookup tables used by the electrical checks and the costing engine.
Amps required | Standard frame |  | Charger kW | Design amps | Breaker A
0 | 400 |  | 30 | 40 | 50
400 | 600 |  | 50 | 72 | 100
600 | 800 |  | 60 | 80 | 100
800 | 1000 |  | 100 | 130 | 200
1000 | 1200 |  | 120 | 160 | 200
1200 | 1600 |  | 160 | 215 | 300
1600 | 2000 |  | 180 | 240 | 300
2000 | 3200 |  | 200 | 265 | 335
3200 | 4000 |  | 240 | 320 | 400
4000 | 5000 |  | 275 | 385 | 500
5000 | 6000 |  | 300 | 400 | 500
6000 | 10000 |  | 360 | 480 | 600
480V SWITCHGEAR AND BREAKER PRICES
Item | Size | Cost
Main | 400A | 20426.82
Main | 800A | 31187
Main | 1000A | 36812.5
Main | 1200A | 43292.68
Main | 1600A | 56750
Main | 2000A | 60000
Main | 2500.0 | 58540
Main | 3000A | 65000
Main | 4000A | 67500
Main | 5000A | 70000
main breakers | 110A | 650
main breakers | 125A | 700
main breakers | 250A | 1100
main breakers | 3000A | 32500
breakers | 100A | 580
breakers | 200A | 900
breakers | 300A | 1450
breakers | 500A | 3100
breakers | 600A | 3700
disconnects | 500A | 4000
CONDUCTOR AND CONDUIT — $ PER FOOT
Wire size | Copper $/ft | Aluminium $/ft | Conduit size | PVC $/ft
10 AWG | 0.30329 | 0.28 | (1/2") | 0.2445
8 AWG | 0.56613 |  | (3/4") | 0.2912
6 AWG | 0.87104 | 0.30636 | (1") | 0.4698
4 AWG | 1.3329 | 0.37998 | (1 1/4") | 0.6155
2 AWG | 2.1044 | 0.36681 | (1 1/2") | 0.7129
1 AWG | 2.3983 | 0.4821 | (2") | 0.8897
1 /0 | 2.953 | 0.66733 | (2 1/2") | 1.396
2 /0 | 3.6376 | 0.75045 | (3") | 1.7033
3 /0 | 4.5658 | 0.88701 | (3 1/2") | 2.25
4 /0 | 5.7305 | 1.0996 | (4") | 2.3164
250 KCMIL | 6.6402 | 1.2278 | (5") | 3.3106
300 KCMIL | 7.9632 | 1.4962
350 KCMIL | 9.3242 | 2.0614
400 KCMIL | 10.6067 | 2.1041
450 KCMIL | 11.334 | 2.7204
500 KCMIL | 13.3006 | 2.7204
600 KCMIL | 16.5738 | 2.7204
750 KCMIL | 25.921 | 4.809
1000 KCMIL | 34.398 | 7.566
CONDUCTOR AMPACITY — NEC Table 310.16
Ampacity at 30 C ambient, not more than three current-carrying conductors in a raceway. Correct for ambient using the table below, then cap the result at the TERMINATION rating per 110.14(C). 450 KCMIL is in this workbook's size list but is not a size Table 310.16 carries, so it is deliberately blank.
Size | Cu-60 | Cu-75 | Cu-90 | Al-60 | Al-75 | Al-90
10 AWG | 30 | 35 | 40 | 25 | 30 | 35
8 AWG | 40 | 50 | 55 | 35 | 40 | 45
6 AWG | 55 | 65 | 75 | 40 | 50 | 55
4 AWG | 70 | 85 | 95 | 55 | 65 | 75
2 AWG | 95 | 115 | 130 | 75 | 90 | 100
1 AWG | 110 | 130 | 145 | 85 | 100 | 115
1 /0 | 125 | 150 | 170 | 100 | 120 | 135
2 /0 | 145 | 175 | 195 | 115 | 135 | 150
3 /0 | 165 | 200 | 225 | 130 | 155 | 175
4 /0 | 195 | 230 | 260 | 150 | 180 | 205
250 KCMIL | 215 | 255 | 290 | 170 | 205 | 230
300 KCMIL | 240 | 285 | 320 | 195 | 230 | 260
350 KCMIL | 260 | 310 | 350 | 210 | 250 | 280
400 KCMIL | 280 | 335 | 380 | 225 | 270 | 305
450 KCMIL
500 KCMIL | 320 | 380 | 430 | 260 | 310 | 350
600 KCMIL | 350 | 420 | 475 | 285 | 340 | 385
750 KCMIL | 400 | 475 | 535 | 320 | 385 | 435
1000 KCMIL | 455 | 545 | 615 | 375 | 445 | 500
AMBIENT TEMPERATURE CORRECTION — NEC Table 310.15(B)(1)(1)
Multiplier on the ampacity above, based on 30 C. "Up to C" is the top of each band; a design ambient is matched to the first band it does not exceed. A blank means that ambient is not permitted for that insulation rating.
Up to C | 60 | 75 | 90
10 | 1.29 | 1.2 | 1.15
15 | 1.22 | 1.15 | 1.12
20 | 1.15 | 1.11 | 1.08
25 | 1.08 | 1.05 | 1.04
30 | 1 | 1 | 1
35 | 0.91 | 0.94 | 0.96
40 | 0.82 | 0.88 | 0.91
45 | 0.71 | 0.82 | 0.87
50 | 0.58 | 0.75 | 0.82
55 | 0.41 | 0.67 | 0.76
60 |  | 0.58 | 0.71
65 |  | 0.47 | 0.65
70 |  | 0.33 | 0.58
75 |  |  | 0.5
80 |  |  | 0.41
CONDUCTOR IMPEDANCE — NEC Chapter 9 Table 9
VERIFY BEFORE RELYING ON THE VOLTAGE DROP. Effective Z at 0.85 power factor, ohms per 1,000 ft, PVC conduit. These figures were typed from memory of the printed table and have NOT been checked against it. The ampacity and correction tables above are trusted; this one is not, and the voltage-drop verdict on the Electrical tab says ADVISORY until an engineer has corrected these rows.
Size | Cu ohm/1000ft | Al ohm/1000ft
10 AWG | 1.2
8 AWG | 0.78
6 AWG | 0.49 | 0.71
4 AWG | 0.31 | 0.45
2 AWG | 0.19 | 0.29
1 AWG | 0.15 | 0.23
1 /0 | 0.12 | 0.19
2 /0 | 0.1 | 0.15
3 /0 | 0.077 | 0.12
4 /0 | 0.062 | 0.1
250 KCMIL | 0.052 | 0.085
300 KCMIL | 0.044 | 0.071
350 KCMIL | 0.038 | 0.061
400 KCMIL | 0.033 | 0.054
450 KCMIL
500 KCMIL | 0.027 | 0.043
600 KCMIL | 0.023 | 0.036
750 KCMIL | 0.019 | 0.029
1000 KCMIL | 0.015 | 0.023
STANDARD OVERCURRENT DEVICE RATINGS — NEC 240.6(A)
15
20
25
30
35
40
45
50
60
70
80
90
100
110
125
150
175
200
225
250
300
350
400
450
500
600
700
800
1000
1200
1600
2000
2500
3000
4000
5000
6000
MARKET BENCHMARKS — DC fast charging by state
Source: Paren, US EV Fast Charging Report, Q2 2026. Port utilisation is time-based — the share of the day a port delivers energy. The intake and the model read the same rows.
State | Port utilisation | Price to driver $/kWh
United States (average) | 15.76% | 0.538
California | 23.1% | 0.606
District of Columbia | 29.7%
Hawaii | 28.7% | 0.856
Florida | 20.1%
Alaska | 2%
Nebraska |  | 0.428
NEC 250.122 — EQUIPMENT GROUND BY OCPD
UNVERIFIED — transcribed from the project model's own table, not from the printed NEC page. The equipment ground is sized on the DEVICE, not the load. Check it before it goes to an inspector.
OCPD up to (A) | Copper | Aluminium
15 | 14 AWG | 12 AWG
20 | 12 AWG | 10 AWG
60 | 10 AWG | 8 AWG
100 | 8 AWG | 6 AWG
200 | 6 AWG | 4 AWG
300 | 4 AWG | 2 AWG
400 | 3 AWG | 1 AWG
500 | 2 AWG | 1 /0
600 | 1 AWG | 2 /0
800 | 1 /0 | 3 /0
1000 | 2 /0 | 4 /0
1200 | 3 /0 | 250 KCMIL
1600 | 4 /0 | 350 KCMIL
2000 | 250 KCMIL | 400 KCMIL
2500 | 350 KCMIL | 600 KCMIL
3000 | 400 KCMIL | 600 KCMIL
4000 | 500 KCMIL | 750 KCMIL

## Utilities
CALIFORNIA ELECTRIC UTILITIES — DELIVERY
Every entity that sets its own retail DELIVERY tariff in California, and therefore its own EV rate. Community choice aggregators are NOT here: a CCA sets the generation component only and cannot set an EV tariff — the delivery utility's tariff still governs in full. CCAs are listed separately below.
Utility | Type | Service territory | EV rate status | DELIVERY UTILITY PICKER — what the Project tab offers | RATE SCHEDULE PICKER — what the Revenue tab offers | Utility (resolved) | Type | Service territory | EV rate status | State
PG&E — Pacific Gas and Electric | IOU | Northern & central CA, 47 counties | EV rate: BEV-1 / BEV-2-S / BEV-2-P | PG&E — Pacific Gas and Electric | BEV-1 | PG&E — Pacific Gas and Electric | IOU | Northern & central CA, 47 counties | EV rate: BEV-1 / BEV-2-S / BEV-2-P | California
SCE — Southern California Edison | IOU | Central & southern CA, 15 counties | EV rate: TOU-EV-7 / 8 / 9 | SCE — Southern California Edison | BEV-2-S | SCE — Southern California Edison | IOU | Central & southern CA, 15 counties | EV rate: TOU-EV-7 / 8 / 9 | California
SDG&E — San Diego Gas & Electric | IOU | San Diego Co. + southern Orange Co. | EV rate: EV-HP | SDG&E — San Diego Gas & Electric | BEV-2-P | SDG&E — San Diego Gas & Electric | IOU | San Diego Co. + southern Orange Co. | EV rate: EV-HP | California
Liberty Utilities (CalPeco Electric) | IOU | North Lake Tahoe & eastern Sierra | EV rate: TOU A-1/A-2/A-3 EV | Liberty Utilities (CalPeco Electric) | TOU-EV-7 | Liberty Utilities (CalPeco Electric) | IOU | North Lake Tahoe & eastern Sierra | EV rate: TOU A-1/A-2/A-3 EV | California
Pacific Power (PacifiCorp) | IOU | Siskiyou, Modoc, Shasta, Del Norte | NO commercial EV rate | Pacific Power (PacifiCorp) | TOU-EV-8 | Pacific Power (PacifiCorp) | IOU | Siskiyou, Modoc, Shasta, Del Norte | NO commercial EV rate | California
Bear Valley Electric Service (BVES) | IOU | Big Bear Lake, San Bernardino Co. | EV rate: TOU-EV-2 / TOU-EV-3 (max 500 kW) | Bear Valley Electric Service (BVES) | TOU-EV-9 | Bear Valley Electric Service (BVES) | IOU | Big Bear Lake, San Bernardino Co. | EV rate: TOU-EV-2 / TOU-EV-3 (max 500 kW) | California
LADWP — Los Angeles Dept of Water & Power | POU | City of Los Angeles + Owens Valley | EV rate: EVA1 / EVA2 / EVA3 (pilot) | LADWP — Los Angeles Dept of Water & Power | EV-HP >150kW | LADWP — Los Angeles Dept of Water & Power | POU | City of Los Angeles + Owens Valley | EV rate: EVA1 / EVA2 / EVA3 (pilot) | California
SMUD — Sacramento Municipal Utility District | POU | Sacramento Co. + part of Placer Co. | EV rate: EV_SR subscription | SMUD — Sacramento Municipal Utility District | EV-HP <150kW | SMUD — Sacramento Municipal Utility District | POU | Sacramento Co. + part of Placer Co. | EV rate: EV_SR subscription | California
IID — Imperial Irrigation District | POU | Imperial Co. + eastern Coachella Valley | NO EV rate | IID — Imperial Irrigation District | UMERC Cg1 — General Secondary, three-phase | IID — Imperial Irrigation District | POU | Imperial Co. + eastern Coachella Valley | NO EV rate | California
MID — Modesto Irrigation District | POU | Modesto & Stanislaus Co. | NO commercial EV rate | MID — Modesto Irrigation District | UMERC Cg5 — General Secondary Time-of-Use | MID — Modesto Irrigation District | POU | Modesto & Stanislaus Co. | NO commercial EV rate | California
Anaheim Public Utilities | POU | City of Anaheim, Orange Co. | EV rate D-EV-2 CLOSED to new customers | Anaheim Public Utilities | UMERC Cg3 — General Secondary Demand TOU | Anaheim Public Utilities | POU | City of Anaheim, Orange Co. | EV rate D-EV-2 CLOSED to new customers | California
Riverside Public Utilities | POU | City of Riverside | EV rate SMEVC capped below 150 kW | Riverside Public Utilities | Manual | Riverside Public Utilities | POU | City of Riverside | EV rate SMEVC capped below 150 kW | California
TID — Turlock Irrigation District | POU | Turlock; Stanislaus, Merced, Tuolumne | NO EV rate | TID — Turlock Irrigation District | REU E2 — Small Commercial (no demand) | TID — Turlock Irrigation District | POU | Turlock; Stanislaus, Merced, Tuolumne | NO EV rate | California
Glendale Water and Power | POU | City of Glendale, LA Co. | NO commercial EV rate | Glendale Water and Power | REU E7/E8 — Large Commercial (demand) | Glendale Water and Power | POU | City of Glendale, LA Co. | NO commercial EV rate | California
Roseville Electric Utility | POU | City of Roseville, Placer Co. | NO commercial EV rate | Roseville Electric Utility |  | Roseville Electric Utility | POU | City of Roseville, Placer Co. | NO commercial EV rate | California
Pasadena Water and Power | POU | City of Pasadena, LA Co. | NO commercial EV rate | Pasadena Water and Power |  | Pasadena Water and Power | POU | City of Pasadena, LA Co. | NO commercial EV rate | California
Silicon Valley Power (Santa Clara) | POU | City of Santa Clara | NO EV rate — by policy | Silicon Valley Power (Santa Clara) |  | Silicon Valley Power (Santa Clara) | POU | City of Santa Clara | NO EV rate — by policy | California
Burbank Water and Power | POU | City of Burbank, LA Co. | NO commercial EV rate | Burbank Water and Power |  | Burbank Water and Power | POU | City of Burbank, LA Co. | NO commercial EV rate | California
Redding Electric Utility | POU | City of Redding, Shasta Co. | Not researched | Redding Electric Utility |  | Redding Electric Utility | POU | City of Redding, Shasta Co. | Not researched | California
Alameda Municipal Power | POU | City of Alameda | NO commercial EV rate | Alameda Municipal Power |  | Alameda Municipal Power | POU | City of Alameda | NO commercial EV rate | California
City of Palo Alto Utilities | POU | City of Palo Alto | NO commercial EV rate | City of Palo Alto Utilities |  | City of Palo Alto Utilities | POU | City of Palo Alto | NO commercial EV rate | California
Lodi Electric Utility | POU | City of Lodi, San Joaquin Co. | Not researched | Lodi Electric Utility |  | Lodi Electric Utility | POU | City of Lodi, San Joaquin Co. | Not researched | California
Colton Public Utilities | POU | City of Colton, San Bernardino Co. | EV rate page exists — obtain tariff | Colton Public Utilities |  | Colton Public Utilities | POU | City of Colton, San Bernardino Co. | EV rate page exists — obtain tariff | California
Azusa Light & Water | POU | City of Azusa, LA Co. | NO commercial EV rate | Azusa Light & Water |  | Azusa Light & Water | POU | City of Azusa, LA Co. | NO commercial EV rate | California
Lompoc Electric Division | POU | City of Lompoc, Santa Barbara Co. | Not researched | Lompoc Electric Division |  | Lompoc Electric Division | POU | City of Lompoc, Santa Barbara Co. | Not researched | California
Truckee Donner PUD | POU | Truckee & Donner, Nevada/Placer Co. | Not researched | Truckee Donner PUD |  | Truckee Donner PUD | POU | Truckee & Donner, Nevada/Placer Co. | Not researched | California
Banning Electric Utility | POU | City of Banning, Riverside Co. | Not researched | Banning Electric Utility |  | Banning Electric Utility | POU | City of Banning, Riverside Co. | Not researched | California
Merced Irrigation District | POU | Merced County | Not researched | Merced Irrigation District |  | Merced Irrigation District | POU | Merced County | Not researched | California
LMUD — Lassen Municipal Utility District | POU | Susanville & Lassen Co. | Not researched | LMUD — Lassen Municipal Utility District |  | LMUD — Lassen Municipal Utility District | POU | Susanville & Lassen Co. | Not researched | California
Ukiah Electric Utility | POU | City of Ukiah, Mendocino Co. | Not researched | Ukiah Electric Utility |  | Ukiah Electric Utility | POU | City of Ukiah, Mendocino Co. | Not researched | California
Trinity Public Utilities District | POU | Trinity County | Not researched | Trinity Public Utilities District |  | Trinity Public Utilities District | POU | Trinity County | Not researched | California
Healdsburg Electric Department | POU | City of Healdsburg, Sonoma Co. | Not researched | Healdsburg Electric Department |  | Healdsburg Electric Department | POU | City of Healdsburg, Sonoma Co. | Not researched | California
Shasta Lake Electric Utility | POU | City of Shasta Lake, Shasta Co. | Not researched | Shasta Lake Electric Utility |  | Shasta Lake Electric Utility | POU | City of Shasta Lake, Shasta Co. | Not researched | California
Rancho Cucamonga Municipal Utility | POU | PARTIAL — newer development only; SCE serves the rest | Not researched | Rancho Cucamonga Municipal Utility |  | Rancho Cucamonga Municipal Utility | POU | PARTIAL — newer development only; SCE serves the rest | Not researched | California
Moreno Valley Utility | POU | PARTIAL — post-2004 development only; SCE serves the rest | Not researched | Moreno Valley Utility |  | Moreno Valley Utility | POU | PARTIAL — post-2004 development only; SCE serves the rest | Not researched | California
Gridley Electric Utility | POU | City of Gridley, Butte Co. | Not researched | Gridley Electric Utility |  | Gridley Electric Utility | POU | City of Gridley, Butte Co. | Not researched | California
Needles Public Utility Authority | POU | City of Needles, San Bernardino Co. | Not researched | Needles Public Utility Authority |  | Needles Public Utility Authority | POU | City of Needles, San Bernardino Co. | Not researched | California
Biggs Municipal Utilities | POU | City of Biggs, Butte Co. | Not researched | Biggs Municipal Utilities |  | Biggs Municipal Utilities | POU | City of Biggs, Butte Co. | Not researched | California
Kirkwood Meadows PUD | POU | Kirkwood ski area, Alpine/Amador/El Dorado | Not researched | Kirkwood Meadows PUD |  | Kirkwood Meadows PUD | POU | Kirkwood ski area, Alpine/Amador/El Dorado | Not researched | California
Shelter Cove Resort Improvement District | POU | Shelter Cove, Humboldt Co. | Not researched | Shelter Cove Resort Improvement District |  | Shelter Cove Resort Improvement District | POU | Shelter Cove, Humboldt Co. | Not researched | California
Hetch Hetchy Power (SFPUC) | POU | SF municipal, SFO, Muni, new development | Not researched | Hetch Hetchy Power (SFPUC) |  | Hetch Hetchy Power (SFPUC) | POU | SF municipal, SFO, Muni, new development | Not researched | California
City of Vernon (Vernon Public Utilities) | POU | Industrial city of Vernon, LA Co. | Not researched | City of Vernon (Vernon Public Utilities) |  | City of Vernon (Vernon Public Utilities) | POU | Industrial city of Vernon, LA Co. | Not researched | California
Corona Department of Water & Power | POU | PARTIAL — limited footprint; SCE serves most of Corona | Not researched | Corona Department of Water & Power |  | Corona Department of Water & Power | POU | PARTIAL — limited footprint; SCE serves most of Corona | Not researched | California
Victorville Municipal Utilities Services | POU | SCLA & industrial Victorville; SCE serves the rest | Not researched | Victorville Municipal Utilities Services |  | Victorville Municipal Utilities Services | POU | SCLA & industrial Victorville; SCE serves the rest | Not researched | California
Island Energy (Pittsburg Power Co.) | POU | Mare Island & Pittsburg | Not researched | Island Energy (Pittsburg Power Co.) |  | Island Energy (Pittsburg Power Co.) | POU | Mare Island & Pittsburg | Not researched | California
Port of Oakland | POU | Port & Oakland Airport tenants | Not researched | Port of Oakland |  | Port of Oakland | POU | Port & Oakland Airport tenants | Not researched | California
Port of Stockton | POU | Port tenants, San Joaquin Co. | Not researched | Port of Stockton |  | Port of Stockton | POU | Port tenants, San Joaquin Co. | Not researched | California
City of Industry | POU | Industrial city, LA Co. | Not researched | City of Industry |  | City of Industry | POU | Industrial city, LA Co. | Not researched | California
Cerritos Electric Utility | POU | Cerritos businesses — SCE still DELIVERS. Verify | Verify delivery tariff with SCE | Cerritos Electric Utility |  | Cerritos Electric Utility | POU | Cerritos businesses — SCE still DELIVERS. Verify | Verify delivery tariff with SCE | California
Lathrop Irrigation District | POU | Parts of Lathrop, San Joaquin Co. | Not researched | Lathrop Irrigation District |  | Lathrop Irrigation District | POU | Parts of Lathrop, San Joaquin Co. | Not researched | California
Aha Macav Power Service (Fort Mojave) | Tribal | Fort Mojave reservation near Needles | Not researched | Aha Macav Power Service (Fort Mojave) |  | Aha Macav Power Service (Fort Mojave) | Tribal | Fort Mojave reservation near Needles | Not researched | California
Plumas-Sierra Rural Electric Cooperative | Co-op | Plumas, Lassen, Sierra counties | Not researched | Plumas-Sierra Rural Electric Cooperative |  | Plumas-Sierra Rural Electric Cooperative | Co-op | Plumas, Lassen, Sierra counties | Not researched | California
Anza Electric Cooperative | Co-op | Anza, Aguanga, Garner Valley, Riverside Co. | Not researched | Anza Electric Cooperative |  | Anza Electric Cooperative | Co-op | Anza, Aguanga, Garner Valley, Riverside Co. | Not researched | California
Surprise Valley Electrification Corp | Co-op | Modoc & Lassen counties | Not researched | Surprise Valley Electrification Corp |  | Surprise Valley Electrification Corp | Co-op | Modoc & Lassen counties | Not researched | California
Valley Electric Association | Co-op | Sliver of eastern Inyo Co. (44 customers) | Not researched | Valley Electric Association |  | Valley Electric Association | Co-op | Sliver of eastern Inyo Co. (44 customers) | Not researched | California
Other / not listed — enter manually | Other |  | Enter the tariff manually on 9_Overrides | DTE Electric Company |  | DTE Electric Company | IOU | Southeast Michigan — Detroit, Ann Arbor, Port Huron | Not researched here | Michigan
|  |  |  | Consumers Energy |  | Consumers Energy | IOU | Most of the Lower Peninsula outside DTE | Not researched here | Michigan
|  |  |  | Indiana Michigan Power (AEP) |  | Indiana Michigan Power (AEP) | IOU | Southwest MI — Berrien, Cass, St Joseph | Not researched here | Michigan
COMMUNITY CHOICE AGGREGATORS — generation only |  |  |  | UMERC — Upper Michigan Energy Resources (We Energies) |  | UMERC — Upper Michigan Energy Resources (We Energies) | IOU | Upper Peninsula — Marquette, Menominee | Not researched here | Michigan
A CCA replaces ONLY the generation $/kWh line. Rate eligibility, time-of-use periods, the demand subscription, facilities charges, Rule 29 treatment and every other charge stay with the delivery utility. Build the bill from the delivery tariff, then substitute the generation line and add PCIA plus the franchise fee surcharge. CCA rebates and make-ready grants are separate cash flows, never a tariff change. |  |  |  | UPPCO — Upper Peninsula Power Company |  | UPPCO — Upper Peninsula Power Company | IOU | Upper Peninsula | Not researched here | Michigan
|  |  |  | Northern States Power — Xcel |  | Northern States Power — Xcel | IOU | Western Upper Peninsula | Not researched here | Michigan
Community choice aggregator |  | Delivery utility |  | Alpena Power Company |  | Alpena Power Company | IOU | Alpena and surrounding townships | Not researched here | Michigan
None — bundled utility service |  | — |  | Lansing Board of Water & Light |  | Lansing Board of Water & Light | POU | Lansing and East Lansing | Not researched here | Michigan
Ava Community Energy (fmr East Bay CE) |  | PG&E |  | Holland Board of Public Works |  | Holland Board of Public Works | POU | City of Holland | Not researched here | Michigan
Clean Power Alliance |  | SCE |  | Traverse City Light & Power |  | Traverse City Light & Power | POU | City of Traverse City | Not researched here | Michigan
Central Coast Community Energy (3CE) |  | PG&E and SCE — depends on address |  | Coldwater Board of Public Utilities |  | Coldwater Board of Public Utilities | POU | City of Coldwater | Not researched here | Michigan
MCE |  | PG&E |  | Wyandotte Municipal Services |  | Wyandotte Municipal Services | POU | City of Wyandotte | Not researched here | Michigan
San Diego Community Power |  | SDG&E |  | Cloverland Electric Cooperative |  | Cloverland Electric Cooperative | Co-op | Eastern Upper Peninsula | Not researched here | Michigan
CleanPowerSF |  | PG&E |  | Great Lakes Energy |  | Great Lakes Energy | Co-op | Northwest Lower Peninsula | Not researched here | Michigan
WestLight Energy (fmr Peninsula Clean Energy) |  | PG&E |  | Presque Isle Electric & Gas Co-op |  | Presque Isle Electric & Gas Co-op | Co-op | Northeast Lower Peninsula | Not researched here | Michigan
San José Clean Energy |  | PG&E |  | HomeWorks Tri-County Electric |  | HomeWorks Tri-County Electric | Co-op | Central Lower Peninsula | Not researched here | Michigan
Silicon Valley Clean Energy |  | PG&E |  | Midwest Energy & Communications |  | Midwest Energy & Communications | Co-op | Southwest Lower Peninsula | Not researched here | Michigan
Clean Energy Alliance |  | SDG&E |  | Thumb Electric Cooperative |  | Thumb Electric Cooperative | Co-op | The Thumb — Huron, Sanilac, Tuscola | Not researched here | Michigan
Sonoma Clean Power |  | PG&E |  | Other / not listed — enter manually |  | Other / not listed — enter manually | Other |  | Enter the tariff manually
Orange County Power Authority |  | SCE
Pioneer Community Energy |  | PG&E
Redwood Coast Energy Authority |  | PG&E
Valley Clean Energy |  | PG&E
Lancaster Energy |  | SCE
Desert Community Energy |  | SCE
Rancho Mirage Energy Authority |  | SCE
Apple Valley Choice Energy |  | SCE
Energy for Palmdale's Independent Choice |  | SCE
King City Community Power |  | PG&E
Pico Rivera Innovative Municipal Energy |  | SCE
Pomona Choice Energy |  | SCE
San Jacinto Power |  | SCE
Santa Barbara Clean Energy |  | SCE
Direct Access ESP (Calpine, Constellation, Shell…) |  | Host IOU
MICHIGAN ELECTRIC UTILITIES — DELIVERY
Service territory in Michigan does not follow a mailing address in any obvious way. Confirm the serving utility against the site address before pricing anything that depends on it.
Utility | Type | Service territory
DTE Electric Company | IOU | Southeast Michigan — Detroit, Ann Arbor, Port Huron
Consumers Energy | IOU | Most of the Lower Peninsula outside DTE
Indiana Michigan Power (AEP) | IOU | Southwest MI — Berrien, Cass, St Joseph
UMERC — Upper Michigan Energy Resources (We Energies) | IOU | Upper Peninsula — Marquette, Menominee
UPPCO — Upper Peninsula Power Company | IOU | Upper Peninsula
Northern States Power — Xcel | IOU | Western Upper Peninsula
Alpena Power Company | IOU | Alpena and surrounding townships
Lansing Board of Water & Light | POU | Lansing and East Lansing
Holland Board of Public Works | POU | City of Holland
Traverse City Light & Power | POU | City of Traverse City
Coldwater Board of Public Utilities | POU | City of Coldwater
Wyandotte Municipal Services | POU | City of Wyandotte
Cloverland Electric Cooperative | Co-op | Eastern Upper Peninsula
Great Lakes Energy | Co-op | Northwest Lower Peninsula
Presque Isle Electric & Gas Co-op | Co-op | Northeast Lower Peninsula
HomeWorks Tri-County Electric | Co-op | Central Lower Peninsula
Midwest Energy & Communications | Co-op | Southwest Lower Peninsula
Thumb Electric Cooperative | Co-op | The Thumb — Huron, Sanilac, Tuscola

## RateLibrary
CALIFORNIA EVSE RATE LIBRARY
Commercial EV and fallback general-service rates, researched 26 August 2026. Read the STATUS column before using any row. VERIFIED means the figure was read in the utility's own published tariff. NOT PUBLISHED means the utility does not publish it — SCE is the significant case, and those rows are deliberately left at zero rather than filled with an estimate. Rates move: re-verify before pricing a project.
Utility | Schedule | From kW | To kW | Voltage | Peak $/kWh | Off-peak $/kWh | Super off $/kWh | Demand $/kW-mo | Block kW | Block $/mo | Overage $/kW | Customer $/mo | Seasons | Time-of-use periods | STATUS | Effective | Source
PG&E — Pacific Gas and Electric | BEV-1 | 0 | 100 | Secondary | 0.35711 | 0.1651 | 0.13844 | 0 | 10 | 12.41 | 2.48 | 0 | None — no seasonal variation | Peak 4-9pm daily; Off 9pm-9am & 2-4pm; Super off 9am-2pm — ALL YEAR | VERIFIED | 2026-03-01 | https://www.pge.com/tariffs/assets/pdf/tariffbook/ELEC_SCHEDS_BEV.pdf
PG&E — Pacific Gas and Electric | BEV-2-S | 100 | 99999 | Secondary | 0.36977 | 0.15654 | 0.13327 | 0 | 50 | 95.56 | 3.82 | 0 | None — no seasonal variation | Peak 4-9pm daily; Off 9pm-9am & 2-4pm; Super off 9am-2pm — ALL YEAR | VERIFIED | 2026-03-01 | https://www.pge.com/tariffs/assets/pdf/tariffbook/ELEC_SCHEDS_BEV.pdf
PG&E — Pacific Gas and Electric | BEV-2-P | 100 | 99999 | Primary | 0.36003 | 0.15115 | 0.12849 | 0 | 50 | 85.98 | 3.44 | 0 | None — no seasonal variation | Peak 4-9pm daily; Off 9pm-9am & 2-4pm; Super off 9am-2pm — ALL YEAR | VERIFIED | 2026-03-01 | https://www.pge.com/tariffs/assets/pdf/tariffbook/ELEC_SCHEDS_BEV.pdf
PG&E — Pacific Gas and Electric | B-20 (non-EV alternative) | 1000 | 99999 | Secondary | 0.17702 | 0.11482 | 0.05872 | 80.43 | 0 | 0 | 0 | 3265 | Summer Jun-Sep / Winter Oct-May | Peak 4-9pm; Super off 9am-2pm MARCH-MAY ONLY | PARTIAL | 2026-03-01 | https://www.pge.com/tariffs/assets/pdf/tariffbook/ELEC_SCHEDS_B-20.pdf
SCE — Southern California Edison | TOU-EV-7 | 0 | 20 | Secondary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Summer Jun-Sep / Winter Oct-May | On-peak 4-9pm summer weekdays | NOT PUBLISHED |  | https://www.sce.com/sites/default/files/custom-files/PDF_Files/TOU-EV-7_8_9_Rate_Fact_Sheet_072025_Accessible.pdf
SCE — Southern California Edison | TOU-EV-8 | 20 | 500 | Secondary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Summer Jun-Sep / Winter Oct-May | On-peak 4-9pm summer weekdays | NOT PUBLISHED |  | https://www.sce.com/sites/default/files/custom-files/PDF_Files/TOU-EV-7_8_9_Rate_Fact_Sheet_072025_Accessible.pdf
SCE — Southern California Edison | TOU-EV-9 | 500 | 99999 | Tiered by voltage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Summer Jun-Sep / Winter Oct-May | On-peak 4-9pm summer weekdays | NOT PUBLISHED |  | https://www.sce.com/sites/default/files/custom-files/PDF_Files/TOU-EV-7_8_9_Rate_Fact_Sheet_072025_Accessible.pdf
SDG&E — San Diego Gas & Electric | EV-HP (<=150 kW) | 20 | 150 | Secondary | 0.32882 | 0.16295 | 0.15307 | 9.43 | 10 | 50.76 | 0 | 151.26 | Summer Jun 1-Oct 31 / Winter Nov 1-May 31 | NOT PUBLISHED — obtain from the tariff sheet | PARTIAL | 2026-08-01 | https://www.sdge.com/sites/default/files/regulatory/Summary%20Table%20for%20Medium%20Comm%208-1-26.pdf
SDG&E — San Diego Gas & Electric | EV-HP (>150 kW) | 150 | 99999 | Secondary | 0.32882 | 0.16295 | 0.15307 | 9.43 | 25 | 126.89 | 0 | 151.26 | Summer Jun 1-Oct 31 / Winter Nov 1-May 31 | NOT PUBLISHED — obtain from the tariff sheet | PARTIAL | 2026-08-01 | https://www.sdge.com/sites/default/files/regulatory/Summary%20Table%20for%20Medium%20Comm%208-1-26.pdf
SDG&E — San Diego Gas & Electric | EV-HP Primary (>150 kW) | 150 | 99999 | Primary | 0.3055 | 0.16257 | 0.15283 | 9.39 | 25 | 126.24 | 0 | 66.15 | Summer Jun 1-Oct 31 / Winter Nov 1-May 31 | NOT PUBLISHED — obtain from the tariff sheet | PARTIAL | 2026-08-01 | https://www.sdge.com/sites/default/files/regulatory/Summary%20Table%20for%20Large%20Comm%208-1-26.pdf
Liberty Utilities (CalPeco Electric) | TOU A-3 EV | 200 | 99999 | All | 0.52239 | 0.30281 | 0 | 0 | 0 | 0 | 0 | 850.81 | Summer / Winter — months NOT PUBLISHED | NOT PUBLISHED — cross-referenced to Special Conditions | PARTIAL | 2026-06-01 | https://california.libertyutilities.com/uploads/CalPeco%20Tariffs/Schedule%20No.%20A-3%20TOU%20EV%20Large%20General%20Service.pdf
Liberty Utilities (CalPeco Electric) | TOU A-2 EV | 0 | 200 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.85 | Summer / Winter — months NOT PUBLISHED | NOT PUBLISHED | PARTIAL | 2026-06-01 | https://california.libertyutilities.com/uploads/CalPeco%20Tariffs/Schedule%20No%20A-2%20TOU%20EV.pdf
Pacific Power (PacifiCorp) | AT-48 Large General TOU | 500 | 99999 | Secondary | 0.14448 | 0.13419 | 0 | 13.45 | 0 | 0 | 0 | 842.62 | None | On-peak adder +0.858c; off-peak credit -0.171c | VERIFIED | 2026-07-10 | https://www.pacificpower.net/content/dam/pcorp/documents/en/pacificpower/rates-regulation/california/CA_Price_Summary.pdf
Pacific Power (PacifiCorp) | A-32 General Service | 20 | 500 | Secondary | 0.20212 | 0.20212 | 0.20212 | 8.5 | 0 | 0 | 0 | 30.54 | None | NO time-of-use differentiation at all | VERIFIED | 2026-06-08 | https://www.pacificpower.net/content/dam/pcorp/documents/en/pacificpower/rates-regulation/california/CA_Price_Summary.pdf
Bear Valley Electric Service (BVES) | TOU-EV-3 | 20 | 500 | All | 0.46315 | 0.37417 | 0.26005 | 9.5 | 0 | 0 | 0 | 0 | Summer / Winter — months NOT PUBLISHED | NOT PUBLISHED | PARTIAL | 2026-09-01 | https://www.bvesinc.com/assets/documents/rates/8-24-26-549-e/schedule-no-tou-ev-3.pdf
SMUD — Sacramento Municipal Utility District | EV_SR tier EV3 (>20% util) | 20 | 99999 | Secondary | 0.2151 | 0.089 | 0.0638 | 0 | 25 | 333 | 0 | 0 | Summer Jun 1-Sep 30 / Non-summer Oct 1-May 31 | Peak 4-9pm weekdays; off-peak saver 9am-4pm non-summer | VERIFIED | 2026-01-01 | https://www.smud.org/-/media/Documents/Rate-Information/Rates/EV-Pilot-Tariff.ashx
SMUD — Sacramento Municipal Utility District | EV_SR tier EV2 (10-20% util) | 20 | 99999 | Secondary | 0.2669 | 0.1088 | 0.0658 | 0 | 25 | 264 | 0 | 0 | Summer Jun 1-Sep 30 / Non-summer Oct 1-May 31 | Peak 4-9pm weekdays; off-peak saver 9am-4pm non-summer | VERIFIED | 2026-01-01 | https://www.smud.org/-/media/Documents/Rate-Information/Rates/EV-Pilot-Tariff.ashx
SMUD — Sacramento Municipal Utility District | EV_SR tier EV1 (<10% util) | 20 | 99999 | Secondary | 0.5198 | 0.2051 | 0.115 | 0 | 25 | 120 | 0 | 0 | Summer Jun 1-Sep 30 / Non-summer Oct 1-May 31 | Peak 4-9pm weekdays; off-peak saver 9am-4pm non-summer | VERIFIED | 2026-01-01 | https://www.smud.org/-/media/Documents/Rate-Information/Rates/EV-Pilot-Tariff.ashx
SMUD — Sacramento Municipal Utility District | CI-TOD4 (non-EV alternative) | 1000 | 99999 | Secondary | 0.2438 | 0.1186 | 0.0788 | 17.66 | 0 | 0 | 0 | 4014.3 | Summer Jun 1-Sep 30 / Non-summer Oct 1-May 31 | Peak 4-9pm weekdays | VERIFIED | 2026-01-01 | https://www.smud.org/-/media/Documents/Rate-Information/Rates/CI-TOD4.ashx
LADWP — Los Angeles Dept of Water & Power | A-2 (2009 base rates) | 30 | 99999 | 4.8 kV | 0.04679 | 0.01879 | 0 | 14 | 0 | 0 | 0 | 25 | High Jun-Sep / Low Oct-May | NOT PUBLISHED | PARTIAL | 2009-07-01 | https://www.ladwp.com/sites/default/files/documents/LADWP_Electric_Rates.pdf
IID — Imperial Irrigation District | TOU-GL | 100 | 99999 | All | 0.2873 | 0.0821 | 0 | 13 | 0 | 0 | 0 | 140 | Summer May-Oct / Winter Nov-Apr | Summer on-peak 4-9pm M-F; winter 5-9am & 5-9pm M-F | VERIFIED | 2026-01-01 | https://www.iid.com/home/showpublisheddocument/22777/638738285500970000
Silicon Valley Power (Santa Clara) | CB-1 TOU | 0 | 4000 | Secondary | 0.1849 | 0.14217 | 0 | 12.14 | 0 | 0 | 0 | 100.45 | None | Peak 6am-10pm Mon-Sat — 16-hour, 6-day window | VERIFIED | 2026-01-01 | https://www.siliconvalleypower.com/home/showpublisheddocument/6251/639032065160570000
Riverside Public Utilities | TOU Large General & Industrial | 150 | 99999 | All | 0.1295 | 0.0907 | 0 | 14.12 | 0 | 0 | 0 | 742.28 | Summer Jun 1-Sep 30 / Winter Oct 1-May 31 | Summer on-peak 12-6pm wkdy; winter on-peak 5-9pm wkdy | VERIFIED | 2026-01-01 | https://www.riversideca.gov/utilities/sites/riversideca.gov.utilities/files/pdf/rates-electric/2024/Electric%20Schedule%20TOU%20-%20Effective%2001-1-24%20Final.pdf
Anaheim Public Utilities | Anaheim Schedule TOU | 500 | 99999 | <=50 kV | 0.148 | 0.0787 | 0 | 24.34 | 0 | 0 | 0 | 342.12 | Summer Jul 1-Nov 1 / Winter Nov 1-Jul 1 | Summer on-peak 4-9pm wkdy; mid-peak 12-4pm & 9-11pm | VERIFIED | 2023-04-03 | https://local.anaheim.net/docs_agend/questys_pub/40932/40962/40963/41099/41102/2.%20Current%20Electric%20Rates,%20Rules%20and%20Regulations%20Rate%20Schedules%20and%20Rule%20Nos.%2026%20and%202941102.pdf
Glendale Water and Power | PC-1-B TOU | 500 | 99999 | All | 0.3892 | 0.1384 | 0 | 28.3 | 0 | 0 | 0 | 0 | High Jul-Oct / Low Nov-Jun | NOT PUBLISHED — note charge is per kW per DAY | PARTIAL | 2024-01-01 | https://www.glendaleca.gov/government/departments/glendale-water-and-power/rates/large-business-pc-1-electric-rates
Burbank Water and Power | XL-TOU | 1000 | 99999 | All | 0.2131 | 0.0896 | 0 | 20 | 0 | 0 | 0 | 0 | Summer / Winter | NOT PUBLISHED — demand billed per kVA not kW | PARTIAL | 2026-01-01 | https://www.burbankwaterandpower.com/documents/d/guest/Summary-of-Electric-Rates-by-Customer-Type_Commercial_all
Pasadena Water and Power | L-1 Secondary | 0 | 99999 | Secondary | 0.13409 | 0.12489 | 0 | 18.76 | 0 | 0 | 0 | 1500 | Summer / Winter | NOT PUBLISHED | PARTIAL | 2025-10-01 | https://pwp.cityofpasadena.net/wp-content/uploads/2025/09/Summary-Rates-2025_10.pdf
Roseville Electric Utility | GS-4 | 1000 | 99999 | All | 0.1969 | 0.095 | 0 | 11.51 | 0 | 0 | 0 | 0 | Summer / Winter | NOT PUBLISHED | PARTIAL | 2026-07-01 | https://www.roseville.ca.gov/electric_utility/rates/index.php
City of Palo Alto Utilities | E-7 | 1000 | 99999 | All | 0.20068 | 0.12834 | 0.08 | 47.54 | 0 | 0 | 0 | 604 | Summer / Winter | NOT PUBLISHED — two demand charges stack | PARTIAL | 2026-07-01 | https://www.cityofpaloalto.org/files/assets/public/v/5/utilities/rates-schedules-for-utilities/commercial-utility-rates/e-7-tou-effective-2025-07-01.pdf
TID — Turlock Irrigation District | Schedule HT | 500 | 2999 | All | 0.1464 | 0.0892 | 0 | 16 | 0 | 0 | 0 | 300 | Summer / Winter | On-peak 12pm-9pm Mon-Fri | VERIFIED | 2026-01-01 | https://www.tid.org/wp-content/uploads/2024/10/HT-Rate-Tariff-Effective-2025.pdf
Alameda Municipal Power | Schedule A-3 | 500 | 4000 | All | 0.14673 | 0.14673 | 0.14673 | 17.96 | 0 | 0 | 0 | 573.6 | None | Flat, non-TOU | VERIFIED | 2025-07-01 | https://www.alamedamp.com/DocumentCenter/View/1477/A3-Rate-Schedule-Effective-2025-7-1
Azusa Light & Water | Azusa Schedule TOU | 200 | 99999 | All | 0.15455 | 0.07026 | 0 | 12.01 | 0 | 0 | 0 | 42.15 | Summer / Winter | Off-peak demand charge is ZERO | VERIFIED | 2026-06-01 | https://azusaca.gov/DocumentCenter/View/50568/Rules-and-Regulations-6-1-2026
SCE — Southern California Edison | TOU-EV-9 PLACEHOLDER <2kV | 500 | 99999 | Below 2 kV | 0.52398 | 0.13292 | 0.08666 | 0 | 0 | 0 | 0 | 701.42 | Summer Jun-Sep / Winter Oct-May | Summer on-peak 4-9pm wkdy. Winter period boundaries DISPUTED between sources | PLACEHOLDER 2021 VINTAGE | 2021-10-01 | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/energy-division/documents/transportation-electrification/sce-ev-rates-updated-oct-2021.pdf
SCE — Southern California Edison | TOU-EV-9 PLACEHOLDER 2-50kV | 500 | 99999 | 2-50 kV | 0.48076 | 0.12201 | 0.08199 | 0 | 0 | 0 | 0 | 373.12 | Summer Jun-Sep / Winter Oct-May | Summer on-peak 4-9pm wkdy | PLACEHOLDER 2021 VINTAGE | 2021-10-01 | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/energy-division/documents/transportation-electrification/sce-ev-rates-updated-oct-2021.pdf
SCE — Southern California Edison | TOU-EV-8 PLACEHOLDER | 20 | 500 | Secondary | 0.59521 | 0.15808 | 0.09772 | 0 | 0 | 0 | 0 | 194.05 | Summer Jun-Sep / Winter Oct-May | Summer on-peak 4-9pm wkdy | PLACEHOLDER 2021 VINTAGE | 2021-10-01 | https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/energy-division/documents/transportation-electrification/sce-ev-rates-updated-oct-2021.pdf
Redding Electric Utility | E2 — Small Commercial (no demand charge) | 0 | 75 | Secondary | 0.1649 | 0.1649 | 0.1649 | 0 | 0 | 0 | 0 | 70 | None — flat all year | None — REU publishes no commercial time-of-use rate | UNVERIFIED — third-party summary | 2025-01-01 | Third-party tariff summary (nectarclimate.com/rates/redding-electric-utility). REU publishes its Rate Book as a PDF that could not be read directly. VERIFY against the City of Redding Rate Book, Section A, and a recent bill. REU proposed 4.5%/yr increases effective 1 Apr 2026 and adoption is unconfirmed.
Redding Electric Utility | E7/E8 — Large Commercial (demand) | 25 | 99999 | Secondary | 0.1086 | 0.1086 | 0.1086 | 21.5 | 0 | 0 | 0 | 95 | None — flat all year | None — no time-of-use. Demand is set by the highest 15-minute interval in the month | UNVERIFIED — third-party summary | 2025-01-01 | Third-party tariff summary (nectarclimate.com/rates/redding-electric-utility). REU publishes its Rate Book as a PDF that could not be read directly. VERIFY against the City of Redding Rate Book, Section A, and a recent bill. REU proposed 4.5%/yr increases effective 1 Apr 2026 and adoption is unconfirmed.
UTILITY EV CHARGING REBATE AND MAKE-READY PROGRAMMES
Incentives are separate cash flows, not tariff changes. Never model one as a rate reduction, and never bank one that is closed or waitlisted.
Utility | Programme | Status | Amounts
LADWP | Commercial EV Charger Rebate | CLOSED — reopening Oct 2026 | DCFC $20k (50-149kW) / $55k (150-274kW) / $100k (275kW+); +25% in DACs; $2m cap per premises
SMUD | Commercial EV Program | OPEN — first come first served | DCFC $7.5k/handle <50kW; $15k 50-149.9kW; $30k >=150kW. Make-ready: panel $1k, transformer $5k, storage $100/kWh
Riverside Public Utilities | Electrify Riverside | OPEN — first come first served | Up to $10k per DC fast charger; infrastructure 50% of cost up to $50k
Glendale Water and Power | Commercial EV charger rebate | OPEN | Lesser of $50k or 50%; up to $75k/75% for DCFC >=50kW, DACs, public access
Burbank Water and Power | Commercial EV charging rebate | Status not stated | DCFC $5k-$10k/port; $10k-$20k for DAC/public/MFH. Cap $200k or 40 ports
Pasadena Water and Power | Commercial charger rebate | 'Limited time' — status not stated | $4,000 per L2; DCFC double, up to $8,000 per charger
Roseville Electric Utility | Charge Ahead | OPEN — but DCFC is non-profit & multifamily ONLY | DCFC $20k/unit (not available to commercial); transformer $5k, panel $1k
Silicon Valley Power | MFH & Commercial EV incentive | CLOSED — fully subscribed | Up to $150k/site but LEVEL 2 ONLY, no DCFC. Refers DCFC to CALeVIP
City of Palo Alto Utilities | EV charger programme | Non-residential reservations CLOSED | Level 2 only, no DCFC. MFH up to $8k/EVSE, $80k site cap
IID | (none found for commercial) | — | Residential Level 2 only, up to $500
SCE | Charge Ready | CLOSED — agreements had to be signed by 31 Dec 2026 | Level 1 and 2 only; DCFC was never available
Redding Electric Utility | DC Fast Charger Rebate | OPEN — verify funding before relying on it | Up to $6,000 per DC fast charging station, maximum 4 stations per customer. Stations must be separately metered. THE CUSTOMER MUST ASSIGN LCFS CREDITS TO REU — which forecloses the FCI capacity credit on the Carbon tab. The two cannot both be taken.