## Intake
RFC INTAKE — EV Charging Project
Fill the yellow cells only — Panel, Estimate, Revenue, Financing, ADA and Timeline calculate from them.
OUR DETAILS
Company
Prepared by (CPM)
CRA
Phone
Email
PROJECT
Client
Site address
City / AHJ
Utility
Incentive program (CALeVIP, CEC…)
Application / project ID
Date
Scope of work
CHARGERS
Model | Qty | Hardware $/u | Category | Make-ready $ | Hardware $ | Ports
DCFC 200kW | 6
L2 Single 40A | 5
Total chargers
DCFC count
L2 count
Total ports
SITE
Distance to nearest charger (ft) | 100
Spacing per extra charger (ft) | 15
Terrain | flat
Trench length (ft) — overtype if surveyed
INCLUDED SERVICES (Yes / No)
Charger hardware | Yes
Site plan design (AutoCAD) | Yes
SLD / electrical design | Yes
Construction PM (CPM) | Yes
Permitting fees | Yes
Private utility scan (GPR) | Yes
COMMERCIAL TERMS (from the RFC_V18 / Hoopa proposal structure)
Hardware price factor | 1 | 1 = RateCard prices as-is; 1.155 = vendor cost × 1.05 contingency × 1.10 markup
Rebate / incentive amount ($) | 0
Network (EVOLV) fee $/port/month | 39.99
Contract length (years) | 5
Service plan $/year (post-warranty) | 0
Financing APR | 8.39%
Financing term (years) | 5
CBC 11B-812 accessible stalls required
Main gear (auto — Panel sheet)
TOTAL ESTIMATE
CUSTOMER TOTAL (after rebate)
Simple payback (years, revenue + credits)

## Panel
Panel Schedules — auto from Intake (mirrors the app's algorithm, NEC 625 continuous loads at 125%)
PANEL SCHEDULE 1 — 480V SWITCHGEAR (LEVEL 3 / DCFC)
Model | Qty | Breaker A | Circuits | A per circuit | Connected A
DCFC connected amps
+ Transformer primary reflection (raw)
480V bus connected amps
480V bus demand amps (×125%)
Suggested main switchgear (A)
Switchgear price (website catalog)
PANEL SCHEDULE 2 — 208V PANEL (LEVEL 2)
Model | Qty | Breaker A | Circuits | A per circuit | Connected A
208V bus connected amps
208V bus demand amps (×125%)
Suggested 208V panel (A)
Panel type
Panel price
STEP-DOWN TRANSFORMER (480V → 208V, only when both levels exist)
Connected kVA (208V load)
Demand kVA (×125%)
Suggested transformer (kVA)
Transformer price
Primary FLA at 480V (selected TX)
Primary breaker (125% of FLA, next standard)
Primary breaker price
BRANCH BREAKERS
Model | Breaker A | Voltage | Circuits | Unit $ | Total $
Branch breakers total (incl. TX primary)
GEAR TOTAL — switchgear + panel + transformer + breakers
A $0 unit price means no catalog price for that size — add it on the RateCard before quoting.

## Panel 480V
PANEL SCHEDULE
engine — do not edit
| NAME | EV_MAIN | LOCATION | OUTDOOR |  | VOLTAGE | 277 / 480 3PH 4W |  |  | MAIN | [5 empty] | 0
|  |  | FED BY |  |  | ENCLOSURE | NEMA3R |  |  | BUS BAR
|  |  | MOUNTING | SURFACE |  | PANEL TYPE | NF |  |  | MAIN AIC | 65,000
| CKT | DESCRIPTION | BREAKER | POLES | A | B |  | C | POLES | BREAKER | DESCRIPTION | CKT
A | 1 | [10 empty] | 2 | A
B | 3 | [10 empty] | 4 | B | total circuits
C | 5 | [10 empty] | 6 | C
A | 7 | [10 empty] | 8 | A
B | 9 | [10 empty] | 10 | B |  | 1
C | 11 | [10 empty] | 12 | C |  | 2
A | 13 | [10 empty] | 14 | A |  | 3
B | 15 | [10 empty] | 16 | B |  | 4
C | 17 | [10 empty] | 18 | C |  | 5
A | 19 | [10 empty] | 20 | A |  | 6
B | 21 | [10 empty] | 22 | B |  | 7
C | 23 | [10 empty] | 24 | C |  | 8
A | 25 | [10 empty] | 26 | A |  | 9
B | 27 | [10 empty] | 28 | B |  | 10
C | 29 | [10 empty] | 30 | C |  | 11
A | 31 | [10 empty] | 32 | A |  | 12
B | 33 | [10 empty] | 34 | B |  | 13
C | 35 | [10 empty] | 36 | C |  | 14
A | 37 | [10 empty] | 38 | A |  | 15
B | 39 | [10 empty] | 40 | B |  | 16
C | 41 | [10 empty] | 42 | C
A | 43 | [10 empty] | 44 | A
B | 45 | [10 empty] | 46 | B
C | 47 | [10 empty] | 48 | C
|  | TOTAL VA | [6 empty] | TOTAL 3PH VA
|  | DEMAND VA | [6 empty] | TOTAL DEMAND VA
|  | HIGH PH VA | [6 empty] | TOTAL AMP
|  | HIGH PH AMP | [6 empty] | MAIN BREAKER

## Panel 208V
PANEL SCHEDULE
engine — do not edit
| NAME | EV_SUB | LOCATION | OUTDOOR |  | VOLTAGE | 120 / 208 3PH 4W |  |  | MAIN | [5 empty] | 0
|  |  | FED BY |  |  | ENCLOSURE | NEMA3R |  |  | BUS BAR
|  |  | MOUNTING | SURFACE |  | PANEL TYPE | NF |  |  | MAIN AIC | 22,000
| CKT | DESCRIPTION | BREAKER | POLES | A | B |  | C | POLES | BREAKER | DESCRIPTION | CKT
A | 1 | [10 empty] | 2 | A
B | 3 | [10 empty] | 4 | B | total circuits
C | 5 | [10 empty] | 6 | C
A | 7 | [10 empty] | 8 | A
B | 9 | [10 empty] | 10 | B |  | 1
C | 11 | [10 empty] | 12 | C |  | 2
A | 13 | [10 empty] | 14 | A |  | 3
B | 15 | [10 empty] | 16 | B |  | 4
C | 17 | [10 empty] | 18 | C |  | 5
A | 19 | [10 empty] | 20 | A |  | 6
B | 21 | [10 empty] | 22 | B |  | 7
C | 23 | [10 empty] | 24 | C |  | 8
A | 25 | [10 empty] | 26 | A |  | 9
B | 27 | [10 empty] | 28 | B |  | 10
C | 29 | [10 empty] | 30 | C |  | 11
A | 31 | [10 empty] | 32 | A |  | 12
B | 33 | [10 empty] | 34 | B |  | 13
C | 35 | [10 empty] | 36 | C |  | 14
A | 37 | [10 empty] | 38 | A |  | 15
B | 39 | [10 empty] | 40 | B |  | 16
C | 41 | [10 empty] | 42 | C |  | 17
A | 43 | [10 empty] | 44 | A |  | 18
B | 45 | [10 empty] | 46 | B |  | 19
C | 47 | [10 empty] | 48 | C |  | 20
21
|  | TOTAL VA | [6 empty] | TOTAL 3PH VA | [5 empty] | 22
|  | DEMAND VA | [6 empty] | TOTAL DEMAND VA | [5 empty] | 23
|  | HIGH PH VA | [6 empty] | TOTAL AMP | [5 empty] | 24
|  | HIGH PH AMP | [6 empty] | MAIN BREAKER

## Estimate
Budgetary Estimate (auto from Intake + Panel + RateCard)
Structure mirrors the RFC_V18 Costs Internal → Summary chain. For the engineered takeoff use the app's Excel export.
Construction labor days (derived)
Electrical supply & construction
Electrical make-ready (wire, conduit, install hardware)
Switchgear, panels & transformer (Panel sheet)
Trenching / asphalt cut (terrain-adjusted)
Civil (concrete, rebar, wheel stops)
Signage, striping & bollards
Accessible EVCS stalls + ramp (ADA sheet)
Spoils haul-off / dump
Private utility scan (GPR)
Equipment rentals
Permit issuance (AHJ)
Utility application + transformer pad
Construction subtotal
Contingency
Construction total (loaded)
Labor (days × rate, contingency-loaded)
Sales tax on construction
Permit valuation (construction + labor)
Equipment purchase invoice
Charger hardware (RateCard × price factor)
Commissioning
Network (EVOLV) fees — ports × $/mo × contract
Service plan over contract (post-warranty years)
Sales tax on charger hardware
Design invoice
Site plan design (AutoCAD)
SLD / electrical engineering (PE)
Construction PM — hours in col C
Plan check (AHJ, % of valuation for DCFC)
Design subtotal
TOTAL PROJECT COST
Less: rebates / incentives (CALeVIP etc.)
CUSTOMER TOTAL (after rebate)

## Revenue
Revenue & Payback (the Hoopa RFC revenue model, formula-driven)
kWh/day = ports × occupancy × operating hours × charging% × port kW × derate. Credits = LCFS $/kW/yr on DCFC.
Retail price $/kWh | 0.65
Utility cost $/kWh | 0.4
Hours of operation / day | 12
Stall occupancy % | 20%
Charging % per occupied hour | 50%
Carbon credit $/kW/yr (DCFC, LCFS) | 71.6667
Charger derate factor | 0.98
Model | Qty | Ports | kW/port | kWh/day | Rev $/day | Net $/mo | CC $/yr
Totals
Charging net revenue / year
Carbon credits / year (DCFC)
Total annual benefit
Benefit over the contract (flat, no escalation)
Simple payback (years)
Assumptions from the Hoopa RFC 'standard-low' case (20% occupancy). Bump occupancy % for busier sites — their 'medium' case used 45-50%.

## Financing
Financing (DLL-style loan summary)
Loan amount (customer total)
Annual interest rate (Intake)
Term (years, Intake)
Monthly payment
Total of payments
Total interest
Monthly revenue + credits (Revenue sheet)
Net monthly cashflow during the term
Mirrors the DLL amortization summary in the Hoopa RFC (their deal: 8.39% APR × 60 months). Negative net cashflow = the site doesn't cover its own loan yet.

## ADA
Accessible EVCS — CBC 11B-812 (auto from Intake)
Total chargers (from Intake)
Van accessible (12 ft + 5 ft aisle)
Standard accessible (9 ft + 5 ft aisle)
Ambulatory (10 ft, no aisle)
Total accessible stalls
Terrain regrade factor (2% slope rule)
ADA construction cost
CBC Table 11B-228.3.2.1 (2022 CBC — van divisor is 300; verify with your AHJ):
Total EVCS | Van | Standard | Ambulatory
1 – 4 | 1 | 0 | 0
5 – 25 | 1 | 1 | 0
26 – 50 | 1 | 1 | 1
51 – 75 | 1 | 2 | 2
76 – 100 | 1 | 3 | 3
101+ | 1 + 1/300 over 100 | 3 + 1/60 over 100 | 3 + 1/50 over 100
• Slope ≤ 2% in every direction under stalls and aisles — regrading is the big cost on sloped lots.
• EVCS markings must NOT be blue (11B-812.9); stencil 'EV CHARGING ONLY' in 12-in letters.
• ISA signs: none if ≤4 EVCS; van space only for 5-25; all van + standard for 26+. Never on ambulatory.
• Accessible EVCS do NOT count toward regular ADA parking minimums (11B-208.1).
• Charger operable parts must sit 15-48 in from grade with 30×48 in clear floor space.

## Timeline
Schedule estimate (business days, auto from Intake)
Phase | Low | High | Note
Site survey & utility scan
Site plan design (AutoCAD)
SLD / electrical design (PE)
Plan check & permits (AHJ) |  |  | AB 970 clocks 20-40 days; real DCFC plan check 4-12 weeks
Utility application & new service (PARALLEL) |  |  | PG&E/SCE queues 4-12 months — usually the critical path on DCFC sites
Construction
Inspection & commissioning
End-to-end (sequential path vs parallel utility)
≈ months (21 business days/month)

## RateCard
Rate Card — every price the template uses. Edit the yellow cells; formulas follow.
Model | Hardware $/u | Make-ready $/u | Category | Voltage | Breaker A | Circuits/u | Unit input A | Ports/u | kW/port | A/circuit | Terrain | Trench × | Labor × | ADA × | Spoils $/ft
L2 Single | 3000 | 795 | L2 | 208 | 50 | 1 | 37 | 1 | 7.7 | 37 | flat | 1 | 1 | 1 | 5
L2 Single 40A | 4000 | 879 | L2 | 208 | 50 | 1 | 40 | 1 | 8.32 | 40 | sloped | 1.2 | 1.15 | 1.4 | 6
L2 Dual | 7500 | 2367 | L2 | 208 | 125 | 2 | 92.3 | 2 | 19.2 | 92.3 | hilly | 1.5 | 1.3 | 1.7 | 8
L2 Dual 80A | 6500 | 1383 | L2 | 208 | 50 | 2 | 80 | 2 | 8.32 | 40 | rocky | 2.5 | 1.5 | 1.8 | 12
L2 Dual 32A | 5500 | 1198 | L2 | 208 | 40 | 2 | 64 | 2 | 6.656 | 32
DCFC 50kW | 32000 | 1941 | DCFC | 480 | 100 | 1 | 60.1 | 1 | 50 | 60.1
DCFC 60kW | 38000 | 1875 | DCFC | 480 | 100 | 1 | 72.2 | 1 | 60 | 72.2 | Trenching $/ft (flat baseline) | 40.81
DCFC 100kW | 52000 | 2787 | DCFC | 480 | 200 | 1 | 120.3 | 1 | 100 | 120.3 | Contingency % | 10%
DCFC 120kW | 60000 | 2692 | DCFC | 480 | 200 | 1 | 144.3 | 1 | 120 | 144.3 | Sales tax % | 7.25%
DCFC 160kW | 72000 | 4288 | DCFC | 480 | 300 | 1 | 192.5 | 1 | 160 | 192.5 | Labor crew $/day | 2250
DCFC 180kW | 80000 | 4658 | DCFC | 480 | 400 | 1 | 216.5 | 1 | 180 | 216.5 | PM hourly rate (CPM) | 358
DCFC 200kW | 92000 | 5901 | DCFC | 480 | 350 | 1 | 265 | 1 | 200 | 265 | CPM % of construction | 5%
DCFC 240kW | 105000 | 5647 | DCFC | 480 | 400 | 1 | 320 | 1 | 240 | 320 | GPR scan $/day | 1500
DCFC 275kW | 120000 | 7936 | DCFC | 480 | 500 | 1 | 385 | 1 | 275 | 385 | GPR trench-ft per day | 2000
DCFC 300kW | 135000 | 7754 | DCFC | 480 | 500 | 1 | 360.8 | 1 | 300 | 360.8 | ADA van stall $ (flat lot) | 6500
DCFC 360kW | 155000 | 10709 | DCFC | 480 | 600 | 1 | 433 | 1 | 360 | 433 | ADA standard stall $ (flat lot) | 4900
Make-ready $/u = wire, conduit & install hardware (engine-calibrated, ~100-180 ft runs). Gear prices on the Panel sheet. Hardware $/u are budgetary — swap in CTX/vendor quotes. | [10 empty] | ADA ambulatory stall $ (flat lot) | 3500
[11 empty] | ADA ramp $ | 5200
Main switchgear 480V (website catalog) | [10 empty] | Civil mobilization base $ | 2903
Size | Price | [9 empty] | Civil $/DCFC (concrete, rebar, stops) | 758
400 | 20426.82 | [9 empty] | Civil $/L2 | 302
800 | 31187 | [9 empty] | Signage+bollards $/DCFC | 658
1000 | 36812.5 | [9 empty] | Signage $/L2 | 396
1200 | 43292.68 | [9 empty] | Utility transformer pad $ (DCFC) | 5000
1600 | 56750 | [9 empty] | Commissioning $/DCFC | 1500
2000 | 60000 | [9 empty] | Commissioning $/L2 | 250
2500 | 58540 | [9 empty] | Equipment rentals base $ | 3519
3000 | 65000 | [9 empty] | Equipment rentals $/labor-day | 261
4000 | 67500
5000 | 70000
Sub-panel / distribution 208V
Size | Price
150 | 1000
250 | 1120
400 | 1660
600 | 5387
800 | 4650
1000 | 30000
Step-down transformer 208V (kVA)
Size | Price
75 | 2970
112.5 | 3250
150 | 5298
175 | 6000
225 | 7144
300 | 10493
500 | 14500
Branch breakers 480V
Size | Price
100 | 350
125 | 420
150 | 480
175 | 550
200 | 650
225 | 700
250 | 750
300 | 800
350 | 1000
400 | 1200
500 | 1800
600 | 2200
Branch breakers 208V
Size | Price
40 | 60
50 | 75
60 | 90
Standard breaker sizes (NEC 240.6)
15
20
25
30
35
40
45
50
60
70
80
90
100
110
125
150
175
200
225
250
300
350
400
450
500
600
700
800
1000
1200
1600
2000
2500
3000
4000
5000

## Instructions
HOW TO USE THIS TEMPLATE
1. Fill the yellow cells on the Intake sheet: your details, client & program IDs, chargers, site facts, services, commercial terms.
2. Everything else calculates: Panel (sizing + gear pricing at website catalog rates), Panel 480V & Panel 208V (plan-set style
schedules with phase-staggered circuits, ready for the drawing set), Estimate, Revenue & Payback, Financing, ADA and Timeline.
The totals, gear pick and payback show at the bottom of the Intake sheet. Grid capacity: 16 circuits @480V / 24 @208V.
3. Every price lives on the RateCard (yellow) — hardware, gear catalog, labor, tax, contingency. Change there, everything follows.
WHAT WAS FOLDED IN FROM THE REAL RFC_V18 WORKBOOKS (VN Village, Boatman, CCMH, Hoopa, Bartell)
• Costs Internal → Summary structure: per-line contingency, labor loaded with contingency, sales tax on construction and on chargers.
• Hoopa proposal extras: EVOLV network fees ($39.99/port/mo × contract), service plans over contract, hardware price factor
(1.05 contingency × 1.10 markup when starting from vendor cost), rebate/incentive line, customer total after rebate.
• Hoopa revenue model: occupancy × operating hours × charging% × derated port kW; $0.65/kWh retail vs $0.40/kWh utility;
LCFS carbon credits ≈ $71.67/kW/yr on DCFC; simple payback. Their financing: DLL loan at 8.39% APR × 60 months (PMT-based).
• Intake carries the incentive program + application ID (CALeVIP / CEC style: D-00025, H-01007, I-271839…).
WHAT THIS TEMPLATE IS
A budgetary intake + estimate. Make-ready allowances are engine-calibrated per charger (~100-180 ft runs); gear is sized & priced live.
Accuracy target ±15% vs the full RFC Estimator app. For the engineered takeoff — exact NEC wire sizes and the vendor-ready BOM —
build the project in the RFC Estimator web app and use its '⬇ Excel' export.
KEY ASSUMPTIONS (2025-26 CA market, sources on file)
• Buses, breakers and the transformer size at 125% of connected input amps (NEC 625 continuous loads), matching the app.
• Terrain multipliers: trenching ×1.2 sloped / ×1.5 hilly / ×2.5 rocky; ADA regrade ×1.4/×1.7/×1.8 (2% slope rule). Solid rock: quote.
• ADA per CBC 11B-812: van $6.5k, standard $4.9k (shop bid rate), ambulatory $3.5k flat-lot, ramp $5.2k. Markings must NOT be blue.
• Permits: L2-only = streamlined flat fees (AB 1236); DCFC = plan check ≈ 2% of construction valuation + issuance + utility fees.
• Design: site plan $2.5k + $150/charger (+$1k DCFC); SLD $6k + $900/DCFC + $150/L2 (PE). CPM = 5% of construction at $358/h.
• GPR $1,500/day per 2,000 trench-ft. Utility energization on DCFC sites runs 4-12 months and sets the real schedule.
• Charger hardware and 'budgetary' breaker prices are allowances — swap in CTX price-book / vendor quotes on the RateCard.